## I_r (hidden)
NORTHERN REGIONAL LOAD DESPATCH CENTRE
AD HYDRO POWER LIMITED
OUTAGE DUE TO PLANNED SHUTDOWN AND TRIPPING ATTRIBUTED TO SELF BY TRANSMISSION LICENSEE
| DURATION - October' 2023 TO DEC'2025 |  |  | LINE/ ICT OUTAGE DETAILS
| ELEMENT CODE | EVENT NO. | ELEMENT NAME | OUTAGE | RESTORATION | DURATION OF OUTAGE ATTRIBUTABLE TO |  |  |  | Classification/ Category Code | NRLDC CODE |  | REASON OF OUTAGE | Shortfall from the scheduled Generation and Loss of Generation, if any. in kwh | NRLDC REMARKS | Restoration time as specified in Regulation 5 (b) (in days) | Actual restoration time (in days)
|  |  |  | DATE TIME | DATE TIME | ADHPL | OTHERS | System constraint/ Natural calamity/ Militancy | Deemed Available
[6 empty] | @ (T) | # (U) | & ( C ) | * (D)
[6 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min | Code | OPENING | CLOSING
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
Oct | 1 | 1 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-10-07 11:49 | 2023-10-07 16:44 | - | - | - | 0.20486 | OSPT | NR-2310-1305 | NR-2310-1355 | Installation of new Check Energy Meter (Make Secure) at 220 kV Prini Switchyard by M/S Power-Grid India Ltd.Banala Team. | - | Outage period and reason verified as per NRLDC records.
Oct | 2A | 1 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2023-10-19 15:54 | 2023-10-19 16:34 | - | 0.027778 | - | - | OMSU | - | NR-2310-4527 | Tripped due to battery bank/ DCDB supply failure at Phozal end which is owned by HPPTCL hence the outage is not attributable to ADHPL. | - | Outage period and reason verified as per NRLDC records.
Oct | 2B | 2 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-10-19 15:54 | 2023-10-19 16:31 | - | 0.025694 | - | - | OMSU | - | NR-2310-4526 | Tripped due to battery bank/ DCDB supply failure at Phozal end which is owned by HPPTCL hence the outage is not attributable to ADHPL. | - | Outage period and reason verified as per NRLDC records.
Oct | 2B | 3 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-10-19 17:24 | 2023-10-19 18:38 | - | 0.051389 | - | - | SPLU | - | NR-2310-4571 | PLCC maloperation. Tripped due to DT received from Nalagarh end at Phozal substation which is owned by HPPTCL hence the outage is not attributable to ADHPL. | - | Outage period and reason verified as per NRLDC records.
Nov | 1 | 1 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-01 10:07 | 2023-11-01 16:40 | 0.27292 | - | - | - | OSPT | NR-2311-116 | NR-2311-175 | Preventive maintenance work of the 220kV Transmission lines. The planned shutdown for preventive maintenance on daily basis has been approved in the 212th OCC meeting held on 18.10.2023. | - | Verified as per NRLDC OMS records
Nov | 1 | 2 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-02 10:27 | 2023-11-02 16:20 | 0.24514 | - | - | - | OSPT | NR-2311-411 | NR-2311-477 |  | - | Verified as per NRLDC OMS records
Nov | 1 | 3 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-03 10:52 | 2023-11-03 16:38 | 0.24028 | - | - | - | OSPT | NR-2311-707 | NR-2311-768 |  | - | Verified as per NRLDC OMS records
Nov | 1 | 4 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-04 10:10 | 2023-11-04 16:32 | 0.26528 | - | - | - | OSPT | NR-2311-1000 | NR-2311-1093 |  | - | Verified as per NRLDC OMS records
Nov | 1 | 5 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-06 10:15 | 2023-11-06 16:50 | 0.27431 | - | - | - | OSPT | NR-2311-1562 | NR-2311-1633 |  | - | Verified as per NRLDC OMS records
Nov | 1 | 6 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-07 09:57 | 2023-11-07 16:41 | 0.28056 | - | - | - | OSPT | NR-2311-1891 | NR-2311-1974 |  | - | Verified as per NRLDC OMS records
Nov | 1 | 7 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-09 09:51 | 2023-11-09 16:45 | 0.2875 | - | - | - | OSPT | NR-2311-2523 | NR-2311-2577 |  | - | Verified as per NRLDC OMS records
Nov | 1 | 8 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-10 09:35 | 2023-11-10 16:32 | 0.28958 | - | - | - | OSPT | NR-2311-2771 | NR-2311-2883 |  | - | Verified as per NRLDC OMS records
Nov | 1 | 9 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-11 09:52 | 2023-11-11 17:01 | 0.29792 | - | - | - | OSPT | NR-2311-3072 | NR-2311-3150 |  | - | Verified as per NRLDC OMS records
Nov | 1 | 10 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-13 09:53 | 2023-11-13 16:26 | 0.27292 | - | - | - | OSPT | NR-2311-3518 | NR-2311-3586 |  | - | Verified as per NRLDC OMS records
Nov | 1 | 11 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-14 09:47 | 2023-11-14 17:13 | 0.30972 | - | - | - | OSPT | NR-2311-3748 | NR-2311-3830 |  | - | Verified as per NRLDC OMS records
Nov | 1 | 12 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-15 10:10 | 2023-11-15 16:25 | 0.26042 | - | - | - | OSPT | NR-2311-4038 | NR-2311-4110 |  | - | Verified as per NRLDC OMS records
Nov | 1 | 13 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-16 09:23 | 2023-11-16 16:53 | 0.3125 | - | - | - | OSPT | NR-2311-4319 | NR-2311-4381 | Pre-winter preventive maintenance work of 220KV Prini switchyard. Also preventive maintenance work of the 220kV Trans. Lines. The planned shutdown for preventive maintenance on daily basis has been approved in the 212th OCC meeting held on 18.10.2023. | - | Verified as per NRLDC OMS records
Nov | 2A | 14 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2023-11-16 09:27 | 2023-11-16 16:40 | 0.30069 | - | - | - | OSPT | NR-2311-4318 | NR-2311-4380 |  | - | Verified as per NRLDC OMS records
Nov | 1 | 15 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-17 09:22 | 2023-11-17 16:43 | 0.30625 | - | - | - | OSPT | NR-2311-4596 | NR-2311-4671 |  | - | Verified as per NRLDC OMS records
Nov | 2A | 16 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2023-11-17 09:12 | 2023-11-17 16:45 | 0.31458 | - | - | - | OSPT | NR-2311-4597 | NR-2311-4670 |  | - | Verified as per NRLDC OMS records
Nov | 1 | 17 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-18 08:42 | 2023-11-18 16:39 | 0.33125 | - | - | - | OSPT | NR-2311-4841 | NR-2311-4926 |  | - | Verified as per NRLDC OMS records
Nov | 2A | 18 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2023-11-18 08:51 | 2023-11-18 16:32 | 0.32014 | - | - | - | OSPT | NR-2311-4844 | NR-2311-4925 |  | - | Verified as per NRLDC OMS records
Nov | 1 | 19 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-19 08:37 | 2023-11-19 16:11 | 0.31528 | - | - | - | OSPT | NR-2311-5102 | NR-2311-5175 |  | - | Verified as per NRLDC OMS records
Nov | 2A | 20 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2023-11-19 08:39 | 2023-11-19 16:26 | 0.32431 | - | - | - | OSPT | NR-2311-5103 | NR-2311-5176 |  | - | Verified as per NRLDC OMS records
Nov | 1 | 21 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-20 08:58 | 2023-11-20 16:48 | 0.32639 | - | - | - | OSPT | NR-2311-5362 | NR-2311-5492 |  | - | Verified as per NRLDC OMS records
Nov | 2A | 22 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2023-11-20 09:00 | 2023-11-20 17:08 | 0.33889 | - | - | - | OSPT | NR-2311-5363 | NR-2311-5508 |  | - | Verified as per NRLDC OMS records
Nov | 1 | 23 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-21 09:03 | 2023-11-21 17:21 | 0.34583 | - | - | - | OSPT | NR-2311-5708 | NR-2311-5841 |  | - | Verified as per NRLDC OMS records
Nov | 2A | 24 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2023-11-21 09:08 | 2023-11-21 17:22 | 0.34306 | - | - | - | OSPT | NR-2311-5704 | NR-2311-5848 |  | - | Verified as per NRLDC OMS records
Nov | 1 | 25 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-22 08:57 | 2023-11-22 17:15 | 0.34583 | - | - | - | OSPT | NR-2311-6031 | NR-2311-6188 |  | - | Verified as per NRLDC OMS records
Nov | 2A | 26 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2023-11-22 09:05 | 2023-11-22 17:10 | 0.33681 | - | - | - | OSPT | NR-2311-6032 | NR-2311-6187 |  | - | Verified as per NRLDC OMS records
Nov | 1 | 27 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-23 08:50 | 2023-11-23 17:06 | 0.34444 | - | - | - | OSPT | NR-2311-6407 | NR-2311-6535 |  | - | Verified as per NRLDC OMS records
Nov | 2A | 28 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2023-11-23 08:52 | 2023-11-23 17:08 | 0.34444 | - | - | - | OSPT | NR-2311-6406 | NR-2311-6536 |  | - | Verified as per NRLDC OMS records
Nov | 1 | 29 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-24 08:23 | 2023-11-24 17:12 | 0.36736 | - | - | - | OSPT | NR-2311-6727 | NR-2311-6884 |  | - | Verified as per NRLDC OMS records
Nov | 2A | 30 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2023-11-24 08:27 | 2023-11-24 17:14 | 0.36597 | - | - | - | OSPT | NR-2311-6728 | NR-2311-6881 |  | - | Verified as per NRLDC OMS records
Nov | 1 | 31 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-25 09:00 | 2023-11-25 16:54 | 0.32917 | - | - | - | OSPT | NR-2311-7062 | NR-2311-7158 |  | - | Verified as per NRLDC OMS records
Nov | 2A | 32 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2023-11-25 09:08 | 2023-11-25 16:57 | 0.32569 | - | - | - | OSPT | NR-2311-7064 | NR-2311-7159 |  | - | Verified as per NRLDC OMS records
| 2A | 33 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2023-11-27 05:36 | 2023-11-27 07:04 | - | - | 0.061111 | - | GOVC | - | NR-2311-7520 | Tripped due to over voltage. | - | Verified as per NRLDC OMS records
Nov | 2B | 1 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-03 11:35 | 2023-11-03 18:15 | - | 0.27778 | - | - | OSPD | NR-2311-717 | NR-2311-825 | Shutdown availed by PGCIL for re-installation of Aviation Globules. The planned shutdown for preventive maintenance on daily basis has been approved in the 212th OCC meeting held on 18.10.2023. | - | Verified as per NRLDC OMS records
Nov | 2B | 2 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-04 11:08 | 2023-11-04 16:40 | - | 0.23056 | - | - | OSPD | NR-2311-1032 | NR-2311-1097 |  | - | Verified as per NRLDC OMS records
Nov | 1 | 3 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-05 10:15 | 2023-11-05 16:46 | - | 0.27153 | - | - | OSPD | NR-2311-1270 | NR-2311-1343 |  | - | Verified as per NRLDC OMS records
Nov | 2B | 4 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-05 10:21 | 2023-11-05 16:45 | - | 0.26667 | - | - | OSPD | NR-2311-1271 | NR-2311-1344 |  | - | Verified as per NRLDC OMS records
Nov | 2B | 5 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-06 10:34 | 2023-11-06 16:53 | - | 0.26319 | - | - | OSPD | NR-2311-1564 | NR-2311-1643 |  | - | Verified as per NRLDC OMS records
Nov | 2B | 6 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-07 10:19 | 2023-11-07 16:44 | - | 0.26736 | - | - | OSPD | NR-2311-1895 | NR-2311-1972 |  | - | Verified as per NRLDC OMS records
Nov | 1 | 7 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-08 10:08 | 2023-11-08 16:40 | - | 0.27222 | - | - | OSPD | NR-2311-2205 | NR-2311-2287 |  | - | Verified as per NRLDC OMS records
Nov | 2B | 8 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-08 11:04 | 2023-11-08 16:45 | - | 0.23681 | - | - | OSPD | NR-2311-2236 | NR-2311-2285 |  | - | Verified as per NRLDC OMS records
Nov | 2B | 9 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-09 10:21 | 2023-11-09 16:51 | - | 0.27083 | - | - | OSPD | NR-2311-2532 | NR-2311-2581 |  | - | Verified as per NRLDC OMS records
Nov | 2B | 10 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-10 10:23 | 2023-11-10 16:36 | - | 0.25903 | - | - | OSPD | NR-2311-2789 | NR-2311-2882 |  | - | Verified as per NRLDC OMS records
Nov | 2B | 11 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-15 11:03 | 2023-11-15 17:12 | - | 0.25625 | - | - | OSPD | NR-2311-4055 | NR-2311-4121 |  | - | Verified as per NRLDC OMS records
Nov | 2B | 12 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-17 12:31 | 2023-11-17 16:46 | - | 0.17708 | - | - | OSPD | NR-2311-4640 | NR-2311-4678 |  | - | Verified as per NRLDC OMS records
Nov | 2B | 19 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-29 10:42 | 2023-11-29 17:43 | - | 0.29236 | - | - | OSPD | NR-2311-8159 | NR-2311-8226 | Annual Maintenance Of Phozal sub station. | - | Verified as per NRLDC OMS records
Nov | 2A | 20 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2023-11-30 10:35 | 2023-11-30 16:13 | - | 0.23472 | - | - | OSPD | NR-2311-8447 | NR-2311-8524 |  | - | Verified as per NRLDC OMS records
Nov | 2B | 18 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-28 00:07 | 2023-11-28 07:26 | - | - | 0.30486 | - | LVRD | NR-2311-7715 | NR-2311-7765 | Manually opened due to high voltage as per Suo-moto Outage. | - | Verified as per NRLDC OMS records
Nov | 2B | 13 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-25 03:00 | 2023-11-25 04:27 | - | - | 0.060417 | - | GOVC | - | NR-2311-6990 | Line tripped due to overvoltage at Phozal substation. | - | Verified as per NRLDC OMS records
Nov | 2A | 14 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2023-11-27 | 2023-11-27 01:26 | - | - | 0.059722 | - | GOVC | - | NR-2311-7478 |  | - | Verified as per NRLDC OMS records
Nov | 2B | 15 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-11-27 | 2023-11-27 07:51 | - | - | 0.32708 | - | GOVC | - | NR-2311-7529 |  | - | Verified as per NRLDC OMS records
Nov | 2A | 17 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2023-11-28 00:08 | 2023-11-28 00:35 | - | 0.01875 | - | - | GOVC | - | NR-2311-7717 | Tripped on High voltage during opening of 220kV Phozal-Nalagarh line . | - | Verified as per NRLDC OMS records
Dec | 1 | 1 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-12-01 10:04 | 2023-12-01 16:35 | 0.27153 | - | - | - | OSPT | NR-2312-116 | NR-2312-215 | Preventive maintenance work of the 220kV Transmission lines. The planned shutdown for preventive maintenance on daily basis has been approved in the 213th OCC meeting held on 21.11.2023. | - | Outage period and reason verified as per NRLDC records.
Dec | 1 | 2 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-12-02 10:15 | 2023-12-02 16:37 | 0.26528 | - | - | - | OSPT | NR-2312-457 | NR-2312-533 |  | - | Outage period and reason verified as per NRLDC records.
Dec | 1 | 3 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-12-04 09:51 | 2023-12-04 16:45 | 0.2875 | - | - | - | OSPT | NR-2312-1060 | NR-2312-1163 |  | - | Outage period and reason verified as per NRLDC records.
Dec | 1 | 4 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-12-05 10:13 | 2023-12-05 16:52 | 0.27708 | - | - | - | OSPT | NR-2312-1452 | NR-2312-1541 |  | - | Outage period and reason verified as per NRLDC records.
Dec | 1 | 5 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-12-06 10:17 | 2023-12-06 16:21 | 0.25278 | - | - | - | OSPT | NR-2312-1836 | NR-2312-1922 |  | - | Outage period and reason verified as per NRLDC records.
Dec | 1 | 6 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-12-07 10:21 | 2023-12-07 16:34 | 0.25903 | - | - | - | OSPT | NR-2312-2177 | NR-2312-2255 |  | - | Outage period and reason verified as per NRLDC records.
Dec | 1 | 7 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-12-08 10:03 | 2023-12-08 16:32 | 0.27014 | - | - | - | OSPT | NR-2312-2489 | NR-2312-2587 |  | - | Outage period and reason verified as per NRLDC records.
Dec | 1 | 8 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-12-09 10:13 | 2023-12-09 16:17 | 0.25278 | - | - | - | OSPT | NR-2312-2835 | NR-2312-2936 |  | - | Outage period and reason verified as per NRLDC records.
Dec | 1 | 9 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-12-11 10:07 | 2023-12-11 18:15 | 0.33889 | - | - | - | OSPT | NR-2312-3486 | NR-2312-3586 |  | - | Outage period and reason verified as per NRLDC records.
Dec | 1 | 10 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-12-12 09:51 | 2023-12-12 16:51 | 0.29167 | - | - | - | OSPT | NR-2312-3881 | NR-2312-4008 |  | - | Outage period and reason verified as per NRLDC records.
Dec | 1 | 11 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-12-13 09:47 | 2023-12-13 18:25 | 0.35972 | - | - | - | OSPT | NR-2312-4282 | NR-2312-4405 |  | - | Outage period and reason verified as per NRLDC records.
Dec | 1 | 12 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-12-14 09:45 | 2023-12-14 17:35 | 0.32639 | - | - | - | OSPT | NR-2312-4681 | NR-2312-4817 |  | - | Outage period and reason verified as per NRLDC records.
Dec | 1 | 13 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-12-15 09:50 | 2023-12-15 16:40 | 0.28472 | - | - | - | OSPT | NR-2312-5069 | NR-2312-5188 |  | - | Outage period and reason verified as per NRLDC records.
Dec | 1 | 14 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-12-16 09:52 | 2023-12-16 16:38 | 0.28194 | - | - | - | OSPT | NR-2312-5431 | NR-2312-5517 |  | - | Outage period and reason verified as per NRLDC records.
Dec | 1 | 15 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-12-18 10:14 | 2023-12-18 16:57 | 0.27986 | - | - | - | OSPT | NR-2312-6082 | NR-2312-6162 |  | - | Outage period and reason verified as per NRLDC records.
Dec | 1 | 16 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-12-19 09:50 | 2023-12-19 16:39 | 0.28403 | - | - | - | OSPT | NR-2312-6424 | NR-2312-6563 |  | - | Outage period and reason verified as per NRLDC records.
Dec | 1 | 17 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-12-20 10:15 | 2023-12-20 16:32 | 0.26181 | - | - | - | OSPT | NR-2312-6862 | NR-2312-6954 |  | - | Outage period and reason verified as per NRLDC records.
Dec | 1 | 18 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-12-21 09:36 | 2023-12-21 16:37 | 0.29236 | - | - | - | OSPT | NR-2312-7244 | NR-2312-7367 |  | - | Outage period and reason verified as per NRLDC records.
Dec | 1 | 19 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-12-22 09:37 | 2023-12-22 16:34 | 0.28958 | - | - | - | OSPT | NR-2312-7627 | NR-2312-7772 |  | - | Outage period and reason verified as per NRLDC records.
Dec | 1 | 20 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-12-23 10:22 | 2023-12-23 16:33 | 0.25764 | - | - | - | OSPT | NR-2312-8028 | NR-2312-8112 |  | - | Outage period and reason verified as per NRLDC records.
Dec | 1 | 21 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-12-25 09:51 | 2023-12-25 16:30 | 0.27708 | - | - | - | OSPT | NR-2312-8593 | NR-2312-8653 |  | - | Outage period and reason verified as per NRLDC records.
Dec | 1 | 22 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-12-26 10:06 | 2023-12-26 16:38 | 0.27222 | - | - | - | OSPT | NR-2312-8880 | NR-2312-8987 |  | - | Outage period and reason verified as per NRLDC records.
Dec | 1 | 23 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-12-27 09:49 | 2023-12-27 16:47 | 0.29028 | - | - | - | OSPT | NR-2312-9250 | NR-2312-9316 |  | - | Outage period and reason verified as per NRLDC records.
Dec | 1 | 24 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-12-28 09:56 | 2023-12-28 16:29 | 0.27292 | - | - | - | OSPT | NR-2312-9568 | NR-2312-9655 |  | - | Outage period and reason verified as per NRLDC records.
Dec | 1 | 25 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-12-29 10:02 | 2023-12-29 17:02 | 0.29167 | - | - | - | OSPT | NR-2312-9918 | NR-2312-10014 |  | - | Outage period and reason verified as per NRLDC records.
Dec | 1 | 26 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2023-12-30 10:08 | 2023-12-30 16:46 | 0.27639 | - | - | - | OSPT | NR-2312-10257 | NR-2312-10369 |  | - | Outage period and reason verified as per NRLDC records.
JAN | 2B | 1 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-01-01 10:24 | 2024-01-01 16:48 | 0.26667 | - | - | - | OSPT | NR-2401-104 | NR-2401-218 | Preventive maintenance work of the 220kV Transmission lines. The planned shutdown for preventive maintenance on daily basis has been approved in the 214th OCC meeting held on 18.12.2023. | - | Outage period and reason verified as per NRLDC records.
JAN | 2B | 2 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-01-02 10:14 | 2024-01-02 17:18 | 0.29444 | - | - | - | OSPT | NR-2401-428 | NR-2401-572 |  | - | Outage period and reason verified as per NRLDC records.
JAN | 2B | 3 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-01-03 10:30 | 2024-01-03 16:48 | 0.2625 | - | - | - | OSPT | NR-2401-841 | NR-2401-911 |  | - | Outage period and reason verified as per NRLDC records.
JAN | 2B | 4 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-01-04 10:20 | 2024-01-04 17:06 | 0.28194 | - | - | - | OSPT | NR-2401-1195 | NR-2401-1305 |  | - | Outage period and reason verified as per NRLDC records.
JAN | 2B | 5 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-01-05 10:16 | 2024-01-05 16:48 | 0.27222 | - | - | - | OSPT | NR-2401-1545 | NR-2401-1692 |  | - | Outage period and reason verified as per NRLDC records.
JAN | 2B | 6 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-01-06 10:16 | 2024-01-06 16:52 | 0.275 | - | - | - | OSPT | NR-2401-1993 | NR-2401-2073 |  | - | Outage period and reason verified as per NRLDC records.
JAN | 2B | 7 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-01-09 10:31 | 2024-01-09 16:50 | 0.26319 | - | - | - | OSPT | NR-2401-2941 | NR-2401-3085 |  | - | Outage period and reason verified as per NRLDC records.
JAN | 2B | 8 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-01-10 10:26 | 2024-01-10 17:05 | 0.27708 | - | - | - | OSPT | NR-2401-3359 | NR-2401-3499 |  | - | Outage period and reason verified as per NRLDC records.
JAN | 2B | 9 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-01-11 10:07 | 2024-01-11 17:07 | 0.29167 | - | - | - | OSPT | NR-2401-3783 | NR-2401-3917 |  | - | Outage period and reason verified as per NRLDC records.
JAN | 2B | 10 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-01-12 10:23 | 2024-01-12 17:03 | 0.27778 | - | - | - | OSPT | NR-2401-4232 | NR-2401-4375 |  | - | Outage period and reason verified as per NRLDC records.
JAN | 2B | 11 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-01-15 10:04 | 2024-01-15 16:50 | 0.28194 | - | - | - | OSPT | NR-2401-5350 | NR-2401-5503 |  | - | Outage period and reason verified as per NRLDC records.
JAN | 2B | 12 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-01-16 09:58 | 2024-01-16 16:46 | 0.28333 | - | - | - | OSPT | NR-2401-5741 | NR-2401-5855 |  | - | Outage period and reason verified as per NRLDC records.
JAN | 2B | 13 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-01-17 10:20 | 2024-01-17 16:52 | 0.27222 | - | - | - | OSPT | NR-2401-6100 | NR-2401-6250 |  | - | Outage period and reason verified as per NRLDC records.
JAN | 2B | 14 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-01-18 09:50 | 2024-01-18 16:46 | 0.28889 | - | - | - | OSPT | NR-2401-6483 | NR-2401-6633 |  | - | Outage period and reason verified as per NRLDC records.
JAN | 2B | 15 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-01-19 09:32 | 2024-01-19 16:53 | 0.30625 | - | - | - | OSPT | NR-2401-6863 | NR-2401-7015 |  | - | Outage period and reason verified as per NRLDC records.
JAN | 2B | 16 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-01-20 10:38 | 2024-01-20 17:01 | 0.26597 | - | - | - | OSPT | NR-2401-7273 | NR-2401-7389 |  | - | Outage period and reason verified as per NRLDC records.
JAN | 2B | 17 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-01-23 10:34 | 2024-01-23 16:50 | 0.26111 | - | - | - | OSPT | NR-2401-8256 | NR-2401-8380 |  | - | Outage period and reason verified as per NRLDC records.
JAN | 2B | 18 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-01-24 11:03 | 2024-01-24 16:46 | 0.23819 | - | - | - | OSPT | NR-2401-8649 | NR-2401-8788 |  | - | Outage period and reason verified as per NRLDC records.
JAN | 2B | 19 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-01-25 10:43 | 2024-01-25 16:50 | 0.25486 | - | - | - | OSPT | NR-2401-9005 | NR-2401-9184 |  | - | Outage period and reason verified as per NRLDC records.
JAN | 2B | 20 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-01-27 10:11 | 2024-01-27 17:17 | 0.29583 | - | - | - | OSPT | NR-2401-9692 | NR-2401-9800 |  | - | Outage period and reason verified as per NRLDC records.
JAN | 2B | 21 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-01-29 10:22 | 2024-01-29 17:04 | 0.27917 | - | - | - | OSPT | NR-2401-10314 | NR-2401-10452 |  | - | Outage period and reason verified as per NRLDC records.
JAN | 2B | 22 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-01-30 10:16 | 2024-01-30 16:53 | 0.27569 | - | - | - | OSPT | NR-2401-10708 | NR-2401-10812 |  | - | Outage period and reason verified as per NRLDC records.
JAN | 1 | 1 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-01-08 10:55 | 2024-01-08 14:40 | - | 0.15625 | - | - | OSPD | NR-2401-2608 | NR-2401-2649 | First time charging of 220/33 kV,31.5MVA Transformer Bay of HPPTCL at AD Hydro Switchyard in Prini. As the shutdown was availed by HPPTCL hence the outage is not attributable to ADHPL. The supporting documents are attached as 'Annex-I' with the mail. | Nil | Outage period and reason verified as per NRLDC records.
JAN | 2B | 2 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-01-08 10:53 | 2024-01-08 14:31 | - | 0.15139 | - | - | OSPD | NR-2401-2609 | NR-2401-2648 |  | Nil | Outage period and reason verified as per NRLDC records.
FEB | ADHP0003 | 1 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-02-07 10:31 | 2024-02-07 16:41 | 0.25694 | - | - | - | OSPT | NR-2402-2132 | NR-2402-2194 | Preventive maintenance work of the 220kV Transmission lines. The planned shutdown for preventive maintenance on daily basis has been approved in the 215th OCC meeting held on 09.01.2024. | - | Outage period and reason verified as per NRLDC records.
FEB | ADHP0003 | 2 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-02-08 10:27 | 2024-02-08 16:54 | 0.26875 | - | - | - | OSPT | NR-2402-2480 | NR-2402-2574 |  | - | Outage period and reason verified as per NRLDC records.
FEB | ADHP0003 | 3 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-02-09 10:15 | 2024-02-09 16:36 | 0.26458 | - | - | - | OSPT | NR-2402-2829 | NR-2402-2943 |  | - | Outage period and reason verified as per NRLDC records.
FEB | ADHP0003 | 4 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-02-10 09:54 | 2024-02-10 16:51 | 0.28958 | - | - | - | OSPT | NR-2402-3230 | NR-2402-3322 |  | - | Outage period and reason verified as per NRLDC records.
FEB | ADHP0003 | 5 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-02-12 10:04 | 2024-02-12 16:24 | 0.26389 | - | - | - | OSPT | NR-2402-3892 | NR-2402-3998 |  | - | Outage period and reason verified as per NRLDC records.
| ADHP0001 | 6 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-02-12 17:42 | 2024-02-12 18:24 | 0.029167 | - | - | - | SPLU | - | NR-2402-4087 | Circuit Breaker at prini end tripped, due to Direct Trip received from Nalagarh end. However Circuit remained charged from Nalagarh end. PLCC maloperation. | - | Outage period and reason verified as per NRLDC records.
FEB | ADHP0003 | 7 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-02-13 10:04 | 2024-02-13 16:34 | 0.27083 | - | - | - | OSPT | NR-2402-4266 | NR-2402-4419 | Preventive maintenance work of the 220kV Transmission lines. The planned shutdown for preventive maintenance on daily basis has been approved in the 215th OCC meeting held on 09.01.2024. | - | Outage period and reason verified as per NRLDC records.
FEB | ADHP0003 | 8 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-02-14 09:40 | 2024-02-14 17:20 | 0.31944 | - | - | - | OSPT | NR-2402-4649 | NR-2402-4800 |  | - | Outage period and reason verified as per NRLDC records.
FEB | ADHP0003 | 9 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-02-15 09:36 | 2024-02-15 16:46 | 0.29861 | - | - | - | OSPT | NR-2402-5038 | NR-2402-5125 |  | - | Outage period and reason verified as per NRLDC records.
FEB | ADHP0003 | 10 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-02-16 10:10 | 2024-02-16 16:46 | 0.275 | - | - | - | OSPT | NR-2402-5454 | NR-2402-5519 |  | - | Outage period and reason verified as per NRLDC records.
FEB | ADHP0003 | 11 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-02-17 09:53 | 2024-02-17 16:20 | 0.26875 | - | - | - | OSPT | NR-2402-5774 | NR-2402-5879 |  | - | Outage period and reason verified as per NRLDC records.
FEB | ADHP0003 | 12 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-02-22 10:15 | 2024-02-22 16:48 | 0.27292 | - | - | - | OSPT | NR-2402-7427 | NR-2402-7530 | Preventive maintenance work of the 220kV Transmission lines. The planned shutdown for preventive maintenance on daily basis has been approved in the 215th OCC meeting held on 09.01.2024. | - | Outage period and reason verified as per NRLDC records.
FEB | ADHP0003 | 13 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-02-23 10:18 | 2024-02-23 17:15 | 0.28958 | - | - | - | OSPT | NR-2402-7830 | NR-2402-7993 |  | - | Outage period and reason verified as per NRLDC records.
FEB | ADHP0003 | 14 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-02-24 10:10 | 2024-02-24 17:17 | 0.29653 | - | - | - | OSPT | NR-2402-8251 | NR-2402-8373 |  | - | Outage period and reason verified as per NRLDC records.
FEB | ADHP0003 | 15 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-02-26 10:21 | 2024-02-26 16:39 | 0.2625 | - | - | - | OSPT | NR-2402-8980 | NR-2402-9089 |  | - | Outage period and reason verified as per NRLDC records.
FEB | ADHP0003 | 16 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-02-28 10:05 | 2024-02-28 16:55 | 0.28472 | - | - | - | OSPT | NR-2402-9702 | NR-2402-9803 |  | - | Outage period and reason verified as per NRLDC records.
FEB | ADHP0003 | 17 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-02-29 10:14 | 2024-02-29 17:12 | 0.29028 | - | - | - | OSPT | NR-2402-10065 | NR-2402-10170 |  | - | Outage period and reason verified as per NRLDC records.
| ADHP0002 | 1 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2024-02-19 20:08 | 2024-02-19 21:28 | - | 0.055556 | - | - | OMSU | - | NR-2402-6614 | R-Phase of Line ADHP0001 auto reclosed at 20:08 but the Line#ADHP0002 breaker tripped at Phozal end whereas the breaker at Prini end did not trip and the line ADHP0002 remained erergized from Prini end. Fault parameters at Phozal substation: - Phase to ground fault (R-N) R- phase fault current - 942.81 Amp E- phase fault current - 934.34 Amp Fault distance from Phojal end- 19.5 km HPPTCL have not yet enabled the Auto Reclose scheme at their end for lines ADHP0002 & ADHP0003 despite repeated requests. | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0003 | 1 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-03-05 10:10 | 2024-03-05 16:30 | 0.26389 | - | - | - | OSPT | NR-2403-1426 | NR-2403-1501 | Preventive maintenance work of the 220kV Transmission lines. The planned shutdown for preventive maintenance on daily basis has been approved in the 216th OCC meeting held on 12.02.2024. |  | Outage period and reason verified as per NRLDC records.
Mar | ADHP0003 | 1 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-03-06 09:57 | 2024-03-06 16:14 | 0.26181 | - | - | - | OSPT | NR-2403-1710 | NR-2403-1785 |  | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0003 | 2 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-03-07 10:11 | 2024-03-07 16:30 | 0.26319 | - | - | - | OSPT | NR-2403-2035 | NR-2403-2128 |  | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0003 | 3 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-03-09 09:43 | 2024-03-09 16:25 | 0.27917 | - | - | - | OSPT | NR-2403-2610 | NR-2403-2687 |  | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 4 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-03-11 09:27 | 2024-03-11 17:28 | 0.33403 | - | - | - | OSPT | NR-2403-3140 | NR-2403-3324 | Post-winter preventive maintenance work of 220KV Prini switchyard and Preventive maintenance work of the 220kV Transmission lines. The planned shutdown for preventive maintenance on daily basis has been approved in the 216th OCC meeting held on 12.02.2024. | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0002 | 5 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2024-03-11 09:01 | 2024-03-11 17:29 | 0.35278 | - | - | - | OSPT | NR-2403-3137 | NR-2403-3325 |  | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 6 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-03-12 09:20 | 2024-03-12 17:22 | 0.33472 | - | - | - | OSPT | NR-2403-3530 | NR-2403-3710 | Post-winter preventive maintenance work of 220KV Prini switchyard. The planned shutdown for preventive maintenance on daily basis has been approved in the 216th OCC meeting held on 12.02.2024. | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0002 | 7 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2024-03-12 09:22 | 2024-03-12 17:38 | 0.34444 | - | - | - | OSPT | NR-2403-3531 | NR-2403-3709 |  | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 8 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-03-13 09:11 | 2024-03-13 17:16 | 0.33681 | - | - | - | OSPT | NR-2403-3904 | NR-2403-4066 |  | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0002 | 9 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2024-03-13 09:16 | 2024-03-13 17:05 | 0.32569 | - | - | - | OSPT | NR-2403-3903 | NR-2403-4065 |  | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 10 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-03-14 09:17 | 2024-03-14 17:58 | 0.36181 | - | - | - | OSPT | NR-2403-4259 | NR-2403-4445 |  | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0002 | 11 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2024-03-14 09:12 | 2024-03-14 18:00 | 0.36667 | - | - | - | OSPT | NR-2403-4253 | NR-2403-4451 |  | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 12 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-03-15 09:05 | 2024-03-15 17:27 | 0.34861 | - | - | - | OSPT | NR-2403-4616 | NR-2403-4786 | Post-winter preventive maintenance work of 220KV Prini switchyard and Preventive maintenance work of the 220kV Transmission lines. The planned shutdown for preventive maintenance on daily basis has been approved in the 216th OCC meeting held on 12.02.2024. | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0002 | 13 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2024-03-15 09:01 | 2024-03-15 17:29 | 0.35278 | - | - | - | OSPT | NR-2403-4617 | NR-2403-4790 |  | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 14 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-03-16 09:01 | 2024-03-16 17:25 | 0.35 | - | - | - | OSPT | NR-2403-4996 | NR-2403-5169 |  | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0002 | 15 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2024-03-16 09:05 | 2024-03-16 17:29 | 0.35 | - | - | - | OSPT | NR-2403-4995 | NR-2403-5172 |  | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 16 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-03-18 09:22 | 2024-03-18 17:06 | 0.32222 | - | - | - | OSPT | NR-2403-5624 | NR-2403-5786 |  | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0002 | 17 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2024-03-18 09:41 | 2024-03-18 17:17 | 0.31667 | - | - | - | OSPT | NR-2403-5640 | NR-2403-5795 |  | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 18 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-03-19 09:44 | 2024-03-19 17:16 | 0.31389 | - | - | - | OSPT | NR-2403-6016 | NR-2403-6216 |  | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0002 | 19 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2024-03-19 09:30 | 2024-03-19 17:18 | 0.325 | - | - | - | OSPT | NR-2403-6014 | NR-2403-6217 |  | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 20 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-03-20 09:43 | 2024-03-20 17:05 | 0.30694 | - | - | - | OSPT | NR-2403-6414 | NR-2403-6588 |  | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0002 | 21 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2024-03-20 09:25 | 2024-03-20 17:07 | 0.32083 | - | - | - | OSPT | NR-2403-6425 | NR-2403-6592 |  | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 22 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-03-21 10:41 | 2024-03-21 17:11 | 0.27083 | - | - | - | OSPT | NR-2403-6804 | NR-2403-6897 | Preventive maintenance work of the 220kV Transmission lines. The planned shutdown for preventive maintenance on daily basis has been approved in the 216th OCC meeting held on 12.02.2024. | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 23 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-03-22 09:59 | 2024-03-22 16:36 | 0.27569 | - | - | - | OSPT | NR-2403-7073 | NR-2403-7189 |  | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 24 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-03-23 09:57 | 2024-03-23 16:53 | 0.28889 | - | - | - | OSPT | NR-2403-7412 | NR-2403-7489 |  | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 25 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-03-26 10:05 | 2024-03-26 16:59 | 0.2875 | - | - | - | OSPT | NR-2403-8060 | NR-2403-8149 |  | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 26 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-03-27 09:50 | 2024-03-27 16:41 | 0.28542 | - | - | - | OSPT | NR-2403-8307 | NR-2403-8413 |  | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 27 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-03-28 10:43 | 2024-03-28 17:30 | 0.28264 | - | - | - | OSPT | NR-2403-8587 | NR-2403-8668 |  | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 28 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-03-29 10:03 | 2024-03-29 16:37 | 0.27361 | - | - | - | OSPT | NR-2403-8810 | NR-2403-8891 |  | - | Outage period and reason verified as per NRLDC records.
| ADHP0003 | 1 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-05-26 13:21 | 2024-05-26 14:36 | 0.052083 | - | - | - | LEFT | - | NR-2405-6563 | Tripped due to Phase to Ground Fault B-G. Fault Type: B-G . Fault Current: 1.0 kA. Fault Distance :40 kms from Phozal towards Nalagarh. | There was shortfall of 1,67,290 kwh from the schedule. | Outage period and reason verified as per NRLDC records./189 MW Generation loss
| ADHP0001 | 2 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-05-26 13:30 | 2024-05-26 14:12 | 0.029167 | - | - | - | LPPT | - | NR-2405-6560 | R-Phase to ground fault occurred in ADHPL 220 kV AD Hydro (AD)- Nalagarh(PG) (ADHPL) Ckt- 1, Auto Reclose in progress started. Simultaneously, Y-B phase picked up in Zone 2 at 13:30:16.585 hrs. due to which AR Lock Out operated causing tripping of 220 kV AD Hydro(AD)- Nalagarh(PG) (ADHPL) Ckt-1.. Fault Current: 0.8 kA. Fault Distance :168.3 kms from Prini end. |  | Outage period and reason verified as per NRLDC records./189 MW Generation loss
| ADHP0002 | 3 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2024-05-26 13:30 | 2024-05-26 14:55 | 0.059028 | - | - | - | OMST | - | NR-2405-6565 | The C.B at AD Hydro was opened intentionally before charging the 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 from Nalagarh to avoid simultaneous charging of the 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1. |  | Outage period and reason verified as per NRLDC records./189 MW Generation loss
May | ADHP0003 | 4 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-05-30 16:44 | 2024-05-31 16:43 | 0.99931 | - | - | - | LEFT | - | NR-2405-7891 | At Nalagarh end Type of fault: R, Y, B to ground. Fault current: 1944 amps.( R phase). Approximate fault distance from Nalagarh 145.25 km. Fault parameters recorded at Phozal Substation: Fault type :R,Y,B to ground. Fault current: R Phase: 2324A. Y- Phase:2382A. B-Phase: 2180A, Earth: 56.91A. Fault distance: Approx. 25.4KM Top conductor got damaged between tower no. 140 & 141 at Bijli Mahadev | Nil | Outage period and reason verified as per NRLDC records. | 3 | 0.99931
| ADHP0001 | 1 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-06-17 18:25 | 2024-06-17 18:57 | 0.022222 | - | - | - | LPPT | - | NR-2406-4449 | Parameters observed at Prini end :- Fault type- Y-B-G fault. Fault Current :- IY- 867.61 Amp IB - 753.07 Amp IN - 1362.73 Amp Fault distance - 75.52 km from Prini towards Nalagarh | Shortfall of 1,20,850 kwh from the scheduled generation no generation loss as there was no spillage of water. | Outage period and reason verified as per NRLDC records./208 MW Generation loss at ADHPL
| ADHP0003 | 2 | 220 kV Phozal(HP)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-06-17 18:25 | 2024-06-17 19:40 | 0.052083 | - | - | - | LPPT | - | NR-2406-4454 | Parameters observed at Phozal end:- Fault type-Y- B-G fault Fault Current :- IY - 1003.47 Amp IB - 1605.35 Amp IN- 1159.22 Amp Fault distance - 65 km from phozal toward Nalagarh Parameters were observed at NLG End:- Fault type- Y- B-G fault Fault Current - 2.6 k Amp Fault distance - 86.4 km from Nalagarh toward Phozal. |  | Outage period and reason verified as per NRLDC records./208 MW Generation loss at ADHPL
| ADHP0002 | 1 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2024-07-22 16:00 | 2024-07-22 16:36 | 0.025 | - | - | - | LPPT | - | NR-2407-3951 | Fault type: Phase to Phase fault (Y-B), Fault current: Iy = 2.795 kA & Ib = 2.613 kA. Distance: 9.6kms from AD Hydro towards Phozal | - | Outage period and reason verified as per NRLDC records
| ADHP0002 | 1 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2024-08-16 22:50 | 2024-08-16 23:42 | - | 0.036111 | - | - | OMSU | - | NR-2408-2477 | Tripped due to R-G Fault. Fault Current = 2979.01 amp. Distance =17.5 km toward Phozal from Prini end. This portion of line is maintained by HPPTCL and HPPTCL have also not yet enabled the Auto Reclose scheme at their end for lines ADHP0002 & ADHP0003 despite repeated requests. Therefore this outage is not attributable to ADHPL. | Nil | Outage period and reason verified as per NRLDC records
| ADHP0002 | 1 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2024-09-12 06:50 | 2024-09-12 10:30 | 0.15278 | - | - | - | SRMT | - | NR-2409-2279 | Line tripped due to operation of the Bus-A protection relay.Tripping had occurred due to malfunctioning of Module F (R-Phase) of Bus-A protection relay B-90A as spurious current was detected in all the modules i.e. F1 to F8 whereas connections are only in F1 to F6 modules | Nil | Outage period and reason verified as per NRLDC records
Nov | ADHP0001 | 1 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-11-04 09:11 | 2024-11-04 18:11 | 0.375 | - | - | - | OSPT | NR-2411-735 | NR-2411-907 | Pre-snow maintenance of 220kV Switchyard. Preventive maintenance of 220kV Line #1 (Prini- Nalagarh) & 220kV Line # 2A (Prini- Phozal) was also carried out. The planned shutdown for preventive maintenance on daily basis has been approved in the 224th OCC meeting held on 16.10.2024. | Nil | Outage period and reason verified as per NRLDC records.
Nov | ADHP0002 | 2 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2024-11-04 09:23 | 2024-11-04 17:49 | 0.35139 | - | - | - | OSPT | NR-2411-742 | NR-2411-908 |  |  | Outage period and reason verified as per NRLDC records.
Nov | ADHP0001 | 3 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-11-05 09:25 | 2024-11-05 17:36 | 0.34097 | - | - | - | OSPT | NR-2411-1078 | NR-2411-1222 |  |  | Outage period and reason verified as per NRLDC records.
Nov | ADHP0002 | 4 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2024-11-05 09:24 | 2024-11-05 17:37 | 0.34236 | - | - | - | OSPT | NR-2411-1073 | NR-2411-1226 |  |  | Outage period and reason verified as per NRLDC records.
Nov | ADHP0001 | 5 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-11-06 09:12 | 2024-11-06 17:31 | 0.34653 | - | - | - | OSPT | NR-2411-1417 | NR-2411-1557 |  |  | Outage period and reason verified as per NRLDC records.
Nov | ADHP0002 | 6 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2024-11-06 09:06 | 2024-11-06 17:32 | 0.35139 | - | - | - | OSPT | NR-2411-1405 | NR-2411-1558 |  |  | Outage period and reason verified as per NRLDC records.
Nov | ADHP0001 | 7 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-11-07 09:10 | 2024-11-07 17:44 | 0.35694 | - | - | - | OSPT | NR-2411-1747 | NR-2411-1911 |  |  | Outage period and reason verified as per NRLDC records.
Nov | ADHP0002 | 8 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2024-11-07 09:17 | 2024-11-07 17:46 | 0.35347 | - | - | - | OSPT | NR-2411-1748 | NR-2411-1912 |  |  | Outage period and reason verified as per NRLDC records.
Nov | ADHP0001 | 9 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-11-08 09:18 | 2024-11-08 17:43 | 0.35069 | - | - | - | OSPT | NR-2411-2128 | NR-2411-2314 |  |  | Outage period and reason verified as per NRLDC records.
Nov | ADHP0002 | 10 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2024-11-08 09:08 | 2024-11-08 17:44 | 0.35833 | - | - | - | OSPT | NR-2411-2098 | NR-2411-2315 |  |  | Outage period and reason verified as per NRLDC records.
Nov | ADHP0001 | 11 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-11-09 09:11 | 2024-11-09 17:50 | 0.36042 | - | - | - | OSPT | NR-2411-2515 | NR-2411-2656 |  |  | Outage period and reason verified as per NRLDC records.
Nov | ADHP0002 | 12 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2024-11-09 09:14 | 2024-11-09 17:51 | 0.35903 | - | - | - | OSPT | NR-2411-2502 | NR-2411-2657 |  |  | Outage period and reason verified as per NRLDC records.
Nov | ADHP0001 | 13 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-11-10 09:07 | 2024-11-10 17:46 | 0.36042 | - | - | - | OSPT | NR-2411-2836 | NR-2411-2984 |  |  | Outage period and reason verified as per NRLDC records.
Nov | ADHP0002 | 14 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2024-11-10 09:10 | 2024-11-10 17:47 | 0.35903 | - | - | - | OSPT | NR-2411-2838 | NR-2411-2983 |  |  | Outage period and reason verified as per NRLDC records.
Nov | ADHP0001 | 15 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-11-11 08:59 | 2024-11-11 17:49 | 0.36806 | - | - | - | OSPT | NR-2411-3139 | NR-2411-3330 |  |  | Outage period and reason verified as per NRLDC records.
Nov | ADHP0002 | 16 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2024-11-11 09:01 | 2024-11-11 17:50 | 0.36736 | - | - | - | OSPT | NR-2411-3137 | NR-2411-3329 |  |  | Outage period and reason verified as per NRLDC records.
Nov | ADHP0001 | 17 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-11-12 09:07 | 2024-11-12 17:44 | 0.35903 | - | - | - | OSPT | NR-2411-3523 | NR-2411-3704 |  |  | Outage period and reason verified as per NRLDC records.
Nov | ADHP0002 | 18 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2024-11-12 09:09 | 2024-11-12 17:46 | 0.35903 | - | - | - | OSPT | NR-2411-3524 | NR-2411-3714 |  |  | Outage period and reason verified as per NRLDC records.
Nov | ADHP0001 | 19 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-11-13 09:00 | 2024-11-13 17:56 | 0.37222 | - | - | - | OSPT | NR-2411-3925 | NR-2411-4147 |  |  | Outage period and reason verified as per NRLDC records.
Nov | ADHP0002 | 20 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2024-11-13 09:05 | 2024-11-13 17:57 | 0.36944 | - | - | - | OSPT | NR-2411-3920 | NR-2411-4146 |  |  | Outage period and reason verified as per NRLDC records.
Nov | ADHP0001 | 21 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-11-14 09:02 | 2024-11-17 19:00 | 1900-01-02 09:58 | - | - | - | OSPT | NR-2411-4365 | NR-2411-5501 | Pre-snow preventive maintenance of 220kV Switchyard & Restoration work of damaged tower no-140 and shifting of CKT-1 to ERS tower. The planned shutdown for preventive maintenance on daily basis has been approved in the 224th OCC meeting held on 16.10.2024. The intimation of the extension of the shutdown upto 17.11.2024 has been given to NRLDC & HPSLDC on mail dated 15.11.2024 & 16.11.2024. The copy of mail is attached herewith as Annexure III. |  | Outage period and reason verified as per NRLDC records.
Nov | ADHP0002 | 22 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2024-11-14 09:05 | 2024-11-14 17:38 | 0.35625 | - | - | - | OSPT | NR-2411-4366 | NR-2411-4556 | Pre-snow maintenance of 220kV Switchyard. Preventive maintenance of 220kV Line #1 (Prini- Nalagarh) & 220kV Line # 2A (Prini- Phozal) was also carried out. The planned shutdown for preventive maintenance on daily basis has been approved in the 224th OCC meeting held on 16.10.2024. |  | Outage period and reason verified as per NRLDC records.
| ADHP0003 | 23 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2024-11-19 09:15 | 2024-11-29 19:51 | 1900-01-09 10:36 | - | - | - | OSPT | NR-2411-6047 | NR-2411-10386 | Shutdown required on continuous basis for rectification of damaged T.No. 140 at Bijlimahadev (Destringing of CKT 2B ( 220 KV Phozal(HP)- Nallagarh(PG) (ADHPL) Ckt-1 from damaged T.No. 140) The planned shutdown for preventive maintenance on daily basis has been approved in the 224th OCC meeting held on 16.10.2024. |  | Outage period and reason verified as per NRLDC records. | 50 | 10.4417
| ADHP0001 | 24 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-11-30 09:14 | - | - | - | - | - | OSPT | NR-2411-10566 | - | Emergent Shutdown was taken on continuous basis to undertake restringing on tower no. 140 at Bijlimahadev w.e.f 30/11/2024 09:14 hrs to 02/12/2024 18:00 hrs. The intimation of the shutdown has been given to NRLDC on mail dated 29.11.2024. The copy of mail is attached herewith as Annexure IV. |  | Outage period and reason verified as per NRLDC records.
| ADHP0001 | 1 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-11-30 09:14 | 2024-12-02 18:50 | 1900-01-01 09:36 | - | - | - | OSPT | NR-2411-10566 | NR-2412-682 | Emergent Shutdown was taken on continuous basis to undertake restringing on tower no. 140 at Bijlimahadev w.e.f 30/11/2024 09:14 hrs to 02/12/2024 18:00 hrs. The intimation of the shutdown has been given to NRLDC on mail dated 29.11.2024. The copy of mail is attached herewith as Annexure IV. | Nil | Outage period and reason verified as per NRLDC records. | 12 | 2.4
Dec | ADHP0001 | 2 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-12-10 09:43 | 2024-12-10 18:47 | 0.37778 | - | - | - | OSPT | NR-2412-4013 | NR-2412-4185 | Preventive maintenance of 220kV Line #1 (Prini- Nalagarh). The planned shutdown for preventive maintenance on daily basis has been approved in the 225th OCC meeting held on 11.11.2024. |  | Outage period and reason verified as per NRLDC records.
Dec | ADHP0001 | 3 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-12-11 09:51 | 2024-12-11 18:11 | 0.34722 | - | - | - | OSPT | NR-2412-4485 | NR-2412-4687 |  |  | Outage period and reason verified as per NRLDC records.
Dec | ADHP0001 | 4 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-12-12 09:49 | 2024-12-12 16:38 | 0.28403 | - | - | - | OSPT | NR-2412-4979 | NR-2412-5164 |  |  | Outage period and reason verified as per NRLDC records.
Dec | ADHP0001 | 5 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-12-13 09:35 | 2024-12-13 16:51 | 0.30278 | - | - | - | OSPT | NR-2412-5468 | NR-2412-5675 |  |  | Outage period and reason verified as per NRLDC records.
Dec | ADHP0001 | 6 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-12-14 09:47 | 2024-12-14 16:53 | 0.29583 | - | - | - | OSPT | NR-2412-5996 | NR-2412-6165 |  |  | Outage period and reason verified as per NRLDC records.
Dec | ADHP0001 | 7 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-12-16 09:41 | 2024-12-16 17:08 | 0.31042 | - | - | - | OSPT | NR-2412-6942 | NR-2412-7112 |  |  | Outage period and reason verified as per NRLDC records.
Dec | ADHP0001 | 8 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-12-17 09:59 | 2024-12-17 17:08 | 0.29792 | - | - | - | OSPT | NR-2412-7495 | NR-2412-7642 |  |  | Outage period and reason verified as per NRLDC records.
Dec | ADHP0001 | 9 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-12-18 09:34 | 2024-12-18 16:52 | 0.30417 | - | - | - | OSPT | NR-2412-7964 | NR-2412-8137 |  |  | Outage period and reason verified as per NRLDC records.
Dec | ADHP0001 | 10 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-12-19 09:24 | 2024-12-19 17:02 | 0.31806 | - | - | - | OSPT | NR-2412-8412 | NR-2412-8618 |  |  | Outage period and reason verified as per NRLDC records.
Dec | ADHP0001 | 11 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-12-20 09:29 | 2024-12-20 17:15 | 0.32361 | - | - | - | OSPT | NR-2412-8950 | NR-2412-9147 |  |  | Outage period and reason verified as per NRLDC records.
Dec | ADHP0001 | 12 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-12-21 09:59 | 2024-12-21 16:50 | 0.28542 | - | - | - | OSPT | NR-2412-9454 | NR-2412-9604 |  |  | Outage period and reason verified as per NRLDC records.
Dec | ADHP0001 | 13 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-12-25 10:06 | 2024-12-25 16:56 | 0.28472 | - | - | - | OSPT | NR-2412-10978 | NR-2412-11101 |  |  | Outage period and reason verified as per NRLDC records.
Dec | ADHP0001 | 14 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-12-26 09:56 | 2024-12-26 17:22 | 0.30972 | - | - | - | OSPT | NR-2412-11341 | NR-2412-11438 |  |  | Outage period and reason verified as per NRLDC records.
Dec | ADHP0001 | 15 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-12-30 10:11 | 2024-12-30 17:25 | 0.30139 | - | - | - | OSPT | NR-2412-12760 | NR-2412-12893 |  |  | Outage period and reason verified as per NRLDC records.
Dec | ADHP0001 | 16 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2024-12-31 10:18 | 2024-12-31 17:45 | 0.31042 |  |  |  | OSPT | NR-2412-13158 | NR-2412-13292 |  |  | Outage period and reason verified as per NRLDC records.
Jan | ADHP0003 | 1 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-01-02 10:17 | 2025-01-02 17:34 | 0.30347 | - | - | - | OSPT | NR-2501-580 | NR-2501-746 | Preventive maintenance of 220kV Line #1 (Prini- Nalagarh). The planned shutdown for preventive maintenance on daily basis has been approved in the 226th OCC meeting held on 13.12.2024. | - | Outage period and reason verified as per NRLDC records.
Jan | ADHP0003 | 2 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-01-02 10:01 | 2025-01-02 17:14 | 0.30069 | - | - | - | OSPT | NR-2501-1036 | NR-2501-1191 |  | - | Outage period and reason verified as per NRLDC records.
Jan | ADHP0003 | 3 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-01-04 10:16 | 2025-01-04 17:34 | 0.30417 | - | - | - | OSPT | NR-2501-1481 | NR-2501-1608 |  | - | Outage period and reason verified as per NRLDC records.
| ADHP0001 | 4 | 220 kV AD Hydro(AD)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-01-06 16:33 | 2025-01-06 16:49 | 0.011111 | - | - | - | LEFT | - | NR-2501-2391 | Tripped due to B phase to ground fault. Fault Current: Ib-0.118 kA & In-0.211 Ka Fault Distance: 96.0 KM | - | Outage period and reason verified as per NRLDC records.
Jan | ADHP0003 | 5 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-01-07 10:26 | 2025-01-07 17:43 | 0.30347 | - | - | - | OSPT | NR-2501-2678 | NR-2501-2812 | Preventive maintenance of 220kV Line #1 (Prini- Nalagarh). The planned shutdown for preventive maintenance on daily basis has been approved in the 226th OCC meeting held on 13.12.2024. | - | Outage period and reason verified as per NRLDC records.
Jan | ADHP0003 | 6 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-01-08 09:52 | 2025-01-08 17:02 | 0.29861 | - | - | - | OSPT | NR-2501-3127 | NR-2501-3271 |  | - | Outage period and reason verified as per NRLDC records.
Jan | ADHP0003 | 7 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-01-09 10:03 | 2025-01-09 16:51 | 0.28333 | - | - | - | OSPT | NR-2501-3575 | NR-2501-3688 |  | - | Outage period and reason verified as per NRLDC records.
Jan | ADHP0003 | 8 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-01-10 10:03 | 2025-01-10 16:35 | 0.27222 | - | - | - | OSPT | NR-2501-4007 | NR-2501-4131 |  | - | Outage period and reason verified as per NRLDC records.
Jan | ADHP0003 | 9 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-01-11 09:45 | 2025-01-11 17:12 | 0.31042 | - | - | - | OSPT | NR-2501-4406 | NR-2501-4536 |  | - | Outage period and reason verified as per NRLDC records.
Jan | ADHP0003 | 10 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-01-14 10:27 | 2025-01-14 16:42 | 0.26042 | - | - | - | OSPT | NR-2501-5421 | NR-2501-5565 |  | - | Outage period and reason verified as per NRLDC records.
Jan | ADHP0003 | 11 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-01-15 10:02 | 2025-01-15 17:18 | 0.30278 | - | - | - | OSPT | NR-2501-5800 | NR-2501-5972 |  | - | Outage period and reason verified as per NRLDC records.
Jan | ADHP0003 | 12 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-01-17 09:30 | 2025-01-17 17:13 | 0.32153 | - | - | - | OSPT | NR-2501-6701 | NR-2501-6884 |  | - | Outage period and reason verified as per NRLDC records.
Jan | ADHP0003 | 13 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-01-18 09:37 | 2025-01-18 17:04 | 0.31042 | - | - | - | OSPT | NR-2501-7143 | NR-2501-7297 |  | - | Outage period and reason verified as per NRLDC records.
Jan | ADHP0003 | 14 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-01-21 10:17 | 2025-01-21 17:17 | 0.29167 | - | - | - | OSPT | NR-2501-8327 | NR-2501-8449 |  | - | Outage period and reason verified as per NRLDC records.
Jan | ADHP0003 | 15 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-01-22 10:08 | 2025-01-22 16:47 | 0.27708 | - | - | - | OSPT | NR-2501-8735 | NR-2501-8856 |  | - | Outage period and reason verified as per NRLDC records.
Jan | ADHP0003 | 16 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-01-23 10:25 | 2025-01-23 17:39 | 0.30139 | - | - | - | OSPT | NR-2501-9144 | NR-2501-9288 |  | - | Outage period and reason verified as per NRLDC records.
Jan | ADHP0003 | 17 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-01-24 10:17 | 2025-01-24 17:05 | 0.28333 | - | - | - | OSPT | NR-2501-9599 | NR-2501-9755 |  | - | Outage period and reason verified as per NRLDC records.
Jan | ADHP0003 | 18 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-01-25 09:51 | 2025-01-25 16:57 | 0.29583 | - | - | - | OSPT | NR-2501-10060 | NR-2501-10197 |  | - | Outage period and reason verified as per NRLDC records.
Jan | ADHP0003 | 19 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-01-27 09:56 | 2025-01-27 17:08 | 0.3 | - | - | - | OSPT | NR-2501-10836 | NR-2501-11015 |  | - | Outage period and reason verified as per NRLDC records.
Jan | ADHP0003 | 20 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-01-28 10:23 | 2025-01-28 17:03 | 0.27778 | - | - | - | OSPT | NR-2501-11295 | NR-2501-11435 |  | - | Outage period and reason verified as per NRLDC records.
Jan | ADHP0003 | 21 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-01-29 09:55 | 2025-01-29 17:18 | 0.30764 | - | - | - | OSPT | NR-2501-11700 | NR-2501-11833 |  | - | Outage period and reason verified as per NRLDC records.
Jan | ADHP0003 | 22 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-01-30 10:08 | 2025-01-30 17:26 | 0.30417 | - | - | - | OSPT | NR-2501-12129 | NR-2501-12246 |  | - | Outage period and reason verified as per NRLDC records.
Jan | ADHP0003 | 23 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-01-31 10:21 | 2025-01-31 17:11 | 0.28472 | - | - | - | OSPT | NR-2501-12570 | NR-2501-12679 |  | - | Outage period and reason verified as per NRLDC records.
| ADHP0003 | 1 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-01-01 11:27 | 2025-01-02 03:21 | - | 0.6625 | - | - | OSPD | NR-2501-199 | NR-2501-417 | For Primary current injection bay wise after Busbar protection relay erection at Nalagarh Sub-Station. The shutdown was requested and availed by CPCC and hence does not pertains to ADHPL. The planned shutdown has been approved in the 226th OCC meeting held on 13.12.2024. | Nil | Outage period and reason verified as per NRLDC records.
| ADHP0001 | 2 | 220 kV AD Hydro(AD)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-01-05 10:28 | 2025-01-05 18:22 | - | 0.32917 | - | - | OSPD | NR-2501-1894 | NR-2501-2014 | For primary current injection bay wise after bus bar protection relay erection at Nalagarh Substation. The shutdown was requested and availed by CPCC and hence does not pertains to ADHPL. The planned shutdown has been approved in the 226th OCC meeting held on 13.12.2024 but the shutdown was postponed to 05.01.2025 from 01.01.2025 for which the ADHPL consent has been given to RTAMC on mail dated 04.01.2025. The copy of mail is attached herewith as Annexure III. |  | Outage period and reason verified as per NRLDC records.
| ADHP0003 | 3 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-01-06 16:33 | 2025-01-06 17:15 | - | 0.029167 | - | - | LEFT | - | NR-2501-2414 | Tripped due to B phase to ground fault. Fault Current: Ib-0.118 kA & In-0.211 Ka Fault Distance: 96.0 KM HPPTCL have not yet enabled the Auto Reclose scheme at their end for lines ADHP0002 & ADHP0003 despite repeated requests. Therefore this outage is not attributable to ADHPL. |  | Outage period and reason verified as per NRLDC records.
Feb | ADHP0003 | 1 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-02-01 09:56 | 2025-02-01 17:04 | 0.29722 | - | - | - | OSPT | NR-2502-135 | NR-2502-268 | Preventive maintenance of 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1. The planned shutdown for preventive maintenance on daily basis has been approved in the 227th OCC meeting held on 16.01.2025. | - | Outage period and reason verified as per NRLDC records.
Feb | ADHP0003 | 2 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-02-03 10:00 | 2025-02-03 17:33 | 0.31458 | - | - | - | OSPT | NR-2502-826 | NR-2502-956 |  | - | Outage period and reason verified as per NRLDC records.
Feb | ADHP0003 | 3 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-02-04 09:53 | 2025-02-04 17:23 | 0.3125 | - | - | - | OSPT | NR-2502-1202 | NR-2502-1382 |  | - | Outage period and reason verified as per NRLDC records.
Feb | ADHP0003 | 4 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-02-06 10:27 | 2025-02-06 17:10 | 0.27986 | - | - | - | OSPT | NR-2502-2123 | NR-2502-2290 |  | - | Outage period and reason verified as per NRLDC records.
Feb | ADHP0003 | 5 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-02-07 09:36 | 2025-02-07 17:07 | 0.31319 | - | - | - | OSPT | NR-2502-2570 | NR-2502-2701 |  | - | Outage period and reason verified as per NRLDC records.
Feb | ADHP0003 | 6 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-02-08 09:35 | 2025-02-08 16:58 | 0.30764 | - | - | - | OSPT | NR-2502-3018 | NR-2502-3161 |  | - | Outage period and reason verified as per NRLDC records.
Feb | ADHP0003 | 7 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-02-09 09:39 | 2025-02-09 17:37 | 0.33194 | - | - | - | OSPT | NR-2502-3437 | NR-2502-3574 |  | - | Outage period and reason verified as per NRLDC records.
Feb | ADHP0003 | 8 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-02-10 09:42 | 2025-02-10 17:12 | 0.3125 | - | - | - | OSPT | NR-2502-3786 | NR-2502-3891 |  | - | Outage period and reason verified as per NRLDC records.
Feb | ADHP0003 | 9 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-02-12 09:41 | 2025-02-12 16:55 | 0.30139 | - | - | - | OSPT | NR-2502-4655 | NR-2502-4837 |  | - | Outage period and reason verified as per NRLDC records.
Feb | ADHP0003 | 10 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-02-13 09:34 | 2025-02-13 16:55 | 0.30625 | - | - | - | OSPT | NR-2502-5065 | NR-2502-5280 |  | - | Outage period and reason verified as per NRLDC records.
Feb | ADHP0003 | 11 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-02-14 09:23 | 2025-02-14 17:04 | 0.32014 | - | - | - | OSPT | NR-2502-5461 | NR-2502-5642 |  | - | Outage period and reason verified as per NRLDC records.
Feb | ADHP0003 | 12 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-02-15 10:12 | 2025-02-15 16:52 | 0.27778 | - | - | - | OSPT | NR-2502-6016 | NR-2502-6135 |  | - | Outage period and reason verified as per NRLDC records.
Feb | ADHP0003 | 13 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-02-17 10:13 | 2025-02-17 16:56 | 0.27986 | - | - | - | OSPT | NR-2502-6891 | NR-2502-7058 |  | - | Outage period and reason verified as per NRLDC records.
Feb | ADHP0003 | 14 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-02-18 09:59 | 2025-02-18 16:47 | 0.28333 | - | - | - | OSPT | NR-2502-7351 | NR-2502-7495 |  | - | Outage period and reason verified as per NRLDC records.
Feb | ADHP0003 | 15 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-02-19 09:49 | 2025-02-19 16:55 | 0.29583 | - | - | - | OSPT | NR-2502-7791 | NR-2502-7925 |  | - | Outage period and reason verified as per NRLDC records.
Feb | ADHP0003 | 16 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-02-21 09:43 | 2025-02-21 17:18 | 0.31597 | - | - | - | OSPT | NR-2502-8617 | NR-2502-8774 |  | - | Outage period and reason verified as per NRLDC records.
| ADHP0003 | 17 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-02-28 18:37 | 2025-03-01 | 5:23 | - | - | - | LPPT | - | - | Fault Parameters:- Three phase to earth fault R- phase fault current - 478.53 Amp , Y- phase fault current - 245.10 Amp, B- phase fault current- 402.00 Amp & Earth Fault current is 746.97 Amp. Fault distance from Phojal end is 39 km. Line is not restored yet. | - | Outage period and reason verified as per NRLDC records.
| ADHP0001 | 18 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-02-28 18:37 | 2025-02-28 19:09 | 0:32 | - | - | - | LPPT | - | NR-2502-11250 | Fault Parameters:- At Prini end: - Fault type - R to B phase to Ground Fault current - 819.122 Amp Fault distance - 45.6 kms. towards Nalagarh from Prini. At Nalagarh end: - Fault type - R to B phase Fault current - 2.031 k Amp Distance - 126.116 km towards Prini. | - | Outage period and reason verified as per NRLDC records.
| ADHP0003 | 1 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-02-28 00:47 | 2025-02-28 15:41 | - | 0.62083 | - | - | LPPT | - | NR-2502-11158 | Fault Parameters:- Fault type - Y phase to B phase Fault current - 1.250 kAmp and 1.246 kAmp Distance -3 km towards Nalagarh The fault location is at distance of 3 km from Phozal towards Nalagarh which is in between ADHPL Tower no. 58 to Phozal substation. This section of the 220 kV line is owned by HPPTCL hence the outage is not attributable to ADHPL. | - | Outage period and reason verified as per NRLDC records.
| ADHP0003 | 1 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-02-28 18:37 | 2025-03-01 17:13 | 0.94167 | - | - | - | LPPT | - | NR-2503-237 | Fault Parameters:- Three phase to earth fault R- phase fault current - 478.53 Amp , Y- phase fault current - 245.10 Amp, B- phase fault current- 402.00 Amp & Earth Fault current is 746.97 Amp. Fault distance from Phojal end is 39 km. | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 2 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-03-05 09:57 | 2025-03-05 17:32 | 0.31597 | - | - | - | OSPT | NR-2503-1545 | NR-2503-1676 | Preventive maintenance of 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1. The planned shutdown for preventive maintenance on daily basis has been approved in the 228th OCC meeting held on 13.02.2025. | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 3 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-03-06 09:53 | 2025-03-06 17:02 | 0.29792 | - | - | - | OSPT | NR-2503-1929 | NR-2503-2053 |  | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 4 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-03-07 10:05 | 2025-03-07 16:50 | 0.28125 | - | - | - | OSPT | NR-2503-2325 | NR-2503-2456 |  | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 5 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-03-08 09:31 | 2025-03-08 17:12 | 0.32014 | - | - | - | OSPT | NR-2503-2793 | NR-2503-2903 |  | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 6 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-03-10 09:05 | 2025-03-10 17:23 | 0.34583 | - | - | - | OSPT | NR-2503-3391 | NR-2503-3632 | Post-winter preventive maintenance of 220kV Prini Switchyard and Transmission Line preventive maintenance The planned shutdown for preventive maintenance on daily basis has been approved in the 228th OCC meeting held on 13.02.2025. | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0002 | 7 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2025-03-10 09:11 | 2025-03-10 17:43 | 0.35556 | - | - | - | OSPT | NR-2503-3400 | NR-2503-3635 |  | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 8 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-03-11 09:07 | 2025-03-11 17:36 | 0.35347 | - | - | - | OSPT | NR-2503-3806 | NR-2503-4014 |  | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 9 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-03-12 09:10 | 2025-03-12 17:05 | 0.32986 | - | - | - | OSPT | NR-2503-4158 | NR-2503-4340 |  | - | Outage period and reason verified as per NRLDC records.
| ADHP0001 | 10 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-03-15 18:34 | 2025-03-15 19:14 | 0.027778 | - | - | - | LEFT | - | NR-2503-5199 | Fault Parameters recorded at ADHPL Switchyard are as under: Fault Type: Phase to Ground fault(B-N). Fault Current: Ib-2.014 kA & In-2.534 Ka Fault Distance: 22.5 KM towards Nalagarh. Line remained charged from AD Hydro end as Auto reclosure operated at AD Hydro end, CB opened at Nalagarh end. | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 11 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-03-18 12:16 | 2025-03-18 17:30 | 0.21806 | - | - | - | OSPT | NR-2503-6044 | NR-2503-6206 | Post-winter preventive maintenance of 220kV Prini Switchyard and Transmission Line preventive maintenance The planned shutdown for preventive maintenance on daily basis has been approved in the 228th OCC meeting held on 13.02.2025. | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0002 | 12 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2025-03-18 12:16 | 2025-03-18 17:41 | 0.22569 | - | - | - | OSPT | NR-2503-6085 | NR-2503-6210 | Post-winter preventive maintenance of 220KV Prini switchyard. The planned shutdown for preventive maintenance on daily basis has been approved in the 228th OCC meeting held on 13.02.2025. | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0002 | 13 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2025-03-19 12:47 | 2025-03-19 17:16 | 0.18681 | - | - | - | OSPT | NR-2503-6497 | NR-2503-6591 |  | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 14 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-03-20 10:11 | 2025-03-20 17:41 | 0.3125 | - | - | - | OSPT | NR-2503-6841 | NR-2503-7023 | Preventive maintenance, reinstallation work for aviation globules & Post -winter preventive maintenance of 220 KV Prini Switchyard. The planned shutdown for preventive maintenance and reinstallation work for aviation globules on daily basis has been approved in the 228th OCC meeting held on 13.02.2025 and the special meeting chaired by NRPC held on 17.02.2025 respectively. MOM of which is attached as Annex-III. | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0002 | 15 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2025-03-20 12:32 | 2025-03-20 17:56 | 0.225 | - | - | - | OSPT | NR-2503-6881 | NR-2503-7022 | Reinstallation work for aviation globules & Post -winter preventive maintenance of 220 KV Prini Switchyard. The planned shutdown for preventive maintenance and reinstallation work for aviation globules on daily basis has been approved in the 228th OCC meeting held on 13.02.2025 and the special meeting chaired by NRPC held on 17.02.2025 respectively. MOM of which is attached as Annex-III. | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0003 | 16 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-03-20 12:18 | 2025-03-20 17:42 | 0.225 | - | - | - | OSPT | NR-2503-6877 | NR-2503-7024 |  | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 17 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-03-21 09:40 | 2025-03-21 17:55 | 0.34375 | - | - | - | OSPT | NR-2503-7256 | NR-2503-7455 |  | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 18 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-03-22 09:48 | 2025-03-22 17:39 | 0.32708 | - | - | - | OSPT | NR-2503-7686 | NR-2503-7812 | Preventive maintenance, reinstallation work for aviation globules. The planned shutdown for preventive maintenance and reinstallation work for aviation globules on daily basis has been approved in the 228th OCC meeting held on 13.02.2025 and the special meeting chaired by NRPC held on 17.02.2025 respectively. MOM of which is attached as Annex-III. | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 19 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-03-24 10:01 | 2025-03-24 17:10 | 0.29792 | - | - | - | OSPT | NR-2503-8321 | NR-2503-8465 |  | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 20 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-03-25 10:02 | 2025-03-25 16:54 | 0.28611 | - | - | - | OSPT | NR-2503-8680 | NR-2503-8768 |  | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 21 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-03-26 10:10 | 2025-03-26 17:02 | 0.28611 | - | - | - | OSPT | NR-2503-9042 | NR-2503-9176 | Preventive maintenance.The planned shutdown for preventive maintenance on daily basis has been approved in the 228th OCC meeting held on 13.02.2025. | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 22 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-03-27 10:11 | 2025-03-27 17:42 | 0.31319 | - | - | - | OSPT | NR-2503-9428 | NR-2503-9574 |  | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 23 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-03-28 10:06 | 2025-03-28 16:38 | 0.27222 | - | - | - | OSPT | NR-2503-9775 | NR-2503-9867 |  | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 24 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-03-29 10:04 | 2025-03-29 17:08 | 0.29444 | - | - | - | OSPT | NR-2503-10113 | NR-2503-10223 |  | - | Outage period and reason verified as per NRLDC records.
Mar | ADHP0003 | 1 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-03-10 11:44 | 2025-03-10 17:08 | - | 0.225 | - | - | OSPD | NR-2503-3513 | NR-2503-3592 | Shutdown availed by CPCC for re-installation of Aviation Globules. The planned shutdown for preventive maintenance on daily basis has been approved in the special meeting chaired by NRPC held on 17.02.2025. MOM of which is attached as Annex-III |  | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 2 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-03-13 12:13 | 2025-03-13 17:16 | - | 0.21042 | - | - | OSPD | NR-2503-4522 | NR-2503-4628 |  |  | Outage period and reason verified as per NRLDC records.
Mar | ADHP0003 | 3 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-03-13 12:20 | 2025-03-13 17:09 | - | 0.20069 | - | - | OSPD | NR-2503-4523 | NR-2503-4627 |  |  | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 4 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-03-14 12:11 | 2025-03-14 17:17 | - | 0.2125 | - | - | OSPD | NR-2503-4779 | NR-2503-4846 |  |  | Outage period and reason verified as per NRLDC records.
Mar | ADHP0003 | 5 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-03-14 12:16 | 2025-03-14 17:08 | - | 0.20278 | - | - | OSPD | NR-2503-4780 | NR-2503-4867 |  |  | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 6 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-03-15 12:09 | 2025-03-15 17:31 | - | 0.22361 | - | - | OSPD | NR-2503-5063 | NR-2503-5187 |  |  | Outage period and reason verified as per NRLDC records.
Mar | ADHP0003 | 7 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-03-15 12:18 | 2025-03-15 17:29 | - | 0.21597 | - | - | OSPD | NR-2503-5062 | NR-2503-5186 |  |  | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 8 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-03-16 11:56 | 2025-03-16 17:14 | - | 0.22083 | - | - | OSPD | NR-2503-5374 | NR-2503-5463 |  |  | Outage period and reason verified as per NRLDC records.
Mar | ADHP0003 | 9 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-03-16 11:58 | 2025-03-16 17:15 | - | 0.22014 | - | - | OSPD | NR-2503-5373 | NR-2503-6462 |  |  | Outage period and reason verified as per NRLDC records.
| ADHP0003 | 10 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-03-16 17:16 | 2025-03-19 17:26 | - | 1900-01-02 00:10 | - | - | OMSU | - | NR-2503-6612 | Phase to Phase Fault Fault parameters received at RTAMC, JAMMU Fault type : Y To B (Phase to phase) Fault Current: 1.5 kamp. Fault Distance: 168.5 km from Nalagarh Fault parameters received at HPPTCL, PHOZAL Fault type: Y To B (Phase to phase). Fault Current: 1.2 kamp. Fault Distance: 2 km from Phozal. Tower Span T-4 To T-5 got snapped. The fault location is at distance of 2 km from Phozal towards Nalagarh which is in between ADHPL Tower no. 58 to Phozal substation. This section of the 220 kV line is owned by HPPTCL hence the outage is not attributable to ADHPL. | - | Outage period and reason verified as per NRLDC records. | 3 | 3.0069
Mar | ADHP0001 | 11 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-03-17 12:20 | 2025-03-17 17:39 | - | 0.22153 | - | - | OSPD | NR-2503-5670 | NR-2503-5771 | Shutdown availed by CPCC for re-installation of Aviation Globules. The planned shutdown for preventive maintenance on daily basis has been approved in the special meeting chaired by NRPC held on 17.02.2025. MOM of which is attached as Annex-III |  | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 12 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-03-19 12:47 | 2025-03-19 17:04 | - | 0.17847 | - | - | OSPD | NR-2503-6484 | NR-2503-6555 |  |  | Outage period and reason verified as per NRLDC records.
Mar | ADHP0003 | 13 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-03-21 12:17 | 2025-03-21 17:56 | - | 0.23542 | - | - | OSPD | NR-2503-7313 | NR-2503-7460 |  |  | Outage period and reason verified as per NRLDC records.
Mar | ADHP0003 | 14 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-03-22 12:20 | 2025-03-22 17:39 | - | 0.22153 | - | - | OSPD | NR-2503-7734 | NR-2503-7814 |  |  | Outage period and reason verified as per NRLDC records.
Mar | ADHP0001 | 15 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-03-23 11:36 | 2025-03-23 17:32 | - | 0.24722 | - | - | OSPD | NR-2503-8057 | NR-2503-8149 |  |  | Outage period and reason verified as per NRLDC records.
Mar | ADHP0003 | 16 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-03-23 11:41 | 2025-03-23 17:23 | - | 0.2375 | - | - | OSPD | NR-2503-8056 | NR-2503-8150 |  |  | Outage period and reason verified as per NRLDC records.
Mar | ADHP0003 | 17 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-03-24 11:58 | 2025-03-24 17:14 | - | 0.21944 | - | - | OSPD | NR-2503-8355 | NR-2503-8470 |  |  | Outage period and reason verified as per NRLDC records.
Mar | ADHP0003 | 18 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-03-25 12:16 | 2025-03-25 16:56 | - | 0.19444 | - | - | OSPD | NR-2503-8701 | NR-2503-8797 |  |  | Outage period and reason verified as per NRLDC records.
| ADHP0001 | 1 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-04-01 09:02 | 2025-04-01 17:15 | 0.34236 | - | - | - | OSPT | NR-2504-79 | NR-2504-204 | Preventive maintenance of 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1. The planned shutdown for preventive maintenance on daily basis has been approved in the 229th OCC meeting held on 11.03.2025. Also the emergent shutdown for Replacement of Generator #2 C.B Poles was availed which was approved through mail dated 31.03.2025. The approval mail is attached as Annex IV. | - | Outage period and reason verified as per NRLDC records.
| ADHP0002 | 2 | 220 kV AD hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2025-04-01 11:09 | 2025-04-01 17:09 | 0.25 | - | - | - | OSPT | NR-2504-139 | NR-2504-202 | The emergent shutdown for Replacement of Generator #2 C.B Poles was availed which was approved through mail dated 31.03.2025. The approval mail is attached as Annex IV. | - | Outage period and reason verified as per NRLDC records.
Apr | ADHP0001 | 3 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-04-02 09:57 | 2025-04-02 16:44 | 0.28264 | - | - | - | OSPT | NR-2504-386 | NR-2504-502 | Preventive maintenance of 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1. The planned shutdown for preventive maintenance on daily basis has been approved in the 229th OCC meeting held on 11.03.2025. | - | Outage period and reason verified as per NRLDC records.
Apr | ADHP0001 | 4 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-04-03 09:58 | 2025-04-03 17:09 | 0.29931 | - | - | - | OSPT | NR-2504-736 | NR-2504-824 |  | - | Outage period and reason verified as per NRLDC records.
Apr | ADHP0001 | 5 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-04-04 10:02 | 2025-04-04 17:09 | 0.29653 | - | - | - | OSPT | NR-2504-1020 | NR-2504-1128 |  | - | Outage period and reason verified as per NRLDC records.
Apr | ADHP0001 | 6 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-04-05 09:32 | 2025-04-05 16:51 | 0.30486 | - | - | - | OSPT | NR-2504-1281 | NR-2504-1378 |  | - | Outage period and reason verified as per NRLDC records.
Apr | ADHP0001 | 7 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-04-07 10:05 | 2025-04-07 17:10 | 0.29514 | - | - | - | OSPT | NR-2504-1734 | NR-2504-1841 |  | - | Outage period and reason verified as per NRLDC records.
Apr | ADHP0001 | 8 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-04-08 09:23 | 2025-04-08 17:05 | 0.32083 | - | - | - | OSPT | NR-2504-2053 | NR-2504-2152 |  | - | Outage period and reason verified as per NRLDC records.
| ADHP0001 | 9 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-04-16 22:51 | 2025-04-16 23:11 | 0.013889 | - | - | - | LEFT | - | NR-2504-4477 | Fault Parameters at Prini end :- Fault Type - CG ( B phase to Ground) Fault Current - 1254 Amp w.r.t ground. Fault distance - 61.7 km towards Nalagarh. Prini end CB remained closed as Auto reclosure operated successfully at ADHPL end. The Auto reclosure operation of Nalagarh end breaker was unsuccessful. | - | Outage period and reason verified as per NRLDC records.
| ADHP0003 | 10 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-04-16 22:51 | 2025-04-16 23:52 | 0.042361 | - | - | - | LPPT | - | NR-2504-4483 | Fault Parameters at Phojal end :- Fault Type - Three phase to Ground Fault Current - R-Phase fault current -388 Amp Y- phase fault current - 102 Amp B- phase fault current- 653 Amp Fault current w.r.t. ground -1045 Amp Fault distance - 70 km towards Nalagarh. | - | Outage period and reason verified as per NRLDC records.
| ADHP0003 | 1 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-04-10 16:16 | 2025-04-10 17:22 | - | 0.045833 | - | - | OMSU | - | NR-2504-2811 | Following Parameters were observed at Phozal end: - Fault type - Line to Earth fault ( B- G ) Fault Current - B - 767 Amp G - 855 Amp Fault distance -68 Km (From Phozal end) Since the Auto reclosure function is not enabled/ implemented at HPPTCL 220kV Phozal substation, Relays will always initiate 3-pole tripping for single phase to ground fault on the line, without taking reclosure attempt for the stated fault on the line, therefore, the above fault is not attributed to the owner ADHPL. ADHPL has been requesting HPPTCL time and again for implementation of Auto - reclosure scheme at Phozal 220kV substation for Line#2A (Phozal-ADHPL) & Line#2B (Phozal-Nalagarh). | - | Outage period and reason verified as per NRLDC records.
| ADHP0001 | 1 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-05-16 15:25 | 2025-05-18 16:01 | - | - | 1900-01-01 00:36 | - | LNCC | - | NR-2505-4938 | Tripped due to Phase to Phase fault ( R - Y ). Fault current 1357 Ampere ( R-Phase ) and 1227 Ampere ( Y-Phase) Breakdown of the 220 kV D/C Line occurred due to falling of a tree on the span between Tower nos. 174 & 175. The middle and lower cross arms of the 220 kV Phozal-Nalagarh Circuit at Tower No.-175 were damaged and all three conductors of the 220 kV AD Hydro-Nalagarh Circuit snapped and fallen down. | There was a shortfall of 10.08 LU on 16.05.2025 & 30.01 LU on 17.05.2025 from the scheduled generation at ADHPL due to this outage. There was Generation Loss of 48.89 LU which includes the shortfall from the scheduled generation due to this outage. Photographs attached in Annex- IV | Outage period and reason verified as per NRLDC records./87 MW Generation Loss observed at AD-Hydro. | 3 | 2.025
| ADHP0003 | 2 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-05-16 15:25 | 2025-05-23 20:46 | - | - | 1900-01-06 05:21 | - | LNCC | - | NR-2505-7014 | Tripped due to Phase to Phase fault ( R - Y ). Fault current 1357 Ampere ( R-Phase ) and 1227 Ampere ( Y-Phase) Breakdown of the 220 kV D/C Line occurred due to falling of a tree on the span between Tower nos. 174 & 175. The middle and lower cross arms of the 220 kV Phozal-Nalagarh Circuit at Tower No.-175 were damaged and all three conductors of the 220 kV AD Hydro-Nalagarh Circuit snapped and fallen down. |  | Outage period and reason verified as per NRLDC records./87 MW Generation Loss observed at AD-Hydro. | 50 | 7.2229
| ADHP0003 | 2 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-05-24 08:56 | 2025-05-24 13:47 | - | - | 0.20208 | - | LNCC | NR-2505-7134 | NR-2505-7208 | Repair work of damaged disc insulators of middle conductor between T.no. 176-177 | - | Outage period and reason verified as per NRLDC records. | 2 | 0.20208
| ADHP0001 | 1 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-06-04 09:09 | 2025-06-04 15:26 | 6:17 | - | - | - | OSPT | NR-2506-947 | NR-2506-1061 | Lopping of overgrown forest tree. The emergent shutdown for the same was availed which was approved through mail dated 02.06.2025. The mail requesting shutdown is attached as Annex IV with the mail. | - | Outage period and reason verified as per NRLDC records.
| ADHP0002 | 2 | 220 kV AD Hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2025-06-05 09:08 | 2025-06-05 13:52 | 4:44 | - | - | - | OSPT | NR-2506-1285 | NR-2506-1363 |  | - | Outage period and reason verified as per NRLDC records.
| ADHP0003 | 3 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-06-13 18:54 | 2025-06-14 14:21 | - | - | 19:27 | - | LNCC | - | NR-2506-3980 | Tripped due to Phase to Phase fault (Y - B) Fault Current :- 2308 Ampere (Y Phase) 1964 Ampere (B Phase) Fault Distance: 35km from Phozal. During line patrolling it was found that one kail tree has uprooted from outside the corridor between T.No.141-142 at Bijlimahadev Photographs attached as Annex- V with the mail. | - | Outage period and reason verified as per NRLDC records.
| ADHP0003 | 4 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-06-17 15:26 | 2025-06-17 23:28 | 8:02 | - | - | - | LHWT | - | NR-2506-4735 | Line tripped due to snapped jumper of Y Phase conductor at Tower No. 178 in Dyar top. Fault Current :- R- Phase Fault current - 310 A Y- Phase fault current - 10 A B- Phase Fault current - 310 A Photographs attached as Annex- VI with the mail. | There was a shortfall of 11.62 LU from the scheduled generation at ADHPL due to this outage. There was Generation Loss of 12.97 LU which includes the shortfall from the scheduled generation due to this outage. | Outage period and reason verified as per NRLDC records./192 MW Generation Loss | 3 | 0.33472
| ADHP0001 | 5 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-06-17 17:09 | 2025-06-17 23:35 | 6:26 | - | - | - | LEFT | - | NR-2506-4736 | Fault Type: B - Phase to Ground Fault. Fault current Ib-1.337 kA & In-1.066 kA. Fault Distance: 63.8 km from AD Hydro. During line patrolling no abnormality was observed. |  | Outage period and reason verified as per NRLDC records./192 MW Generation Loss
| ADHP0001 | 1 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-08-07 16:38 | 2025-08-07 18:12 | - | - | 0.065278 | - | LNCC | - | NR-2508-1772 | Line tripped, following paramters were observed: Fault Type :-Double Phase to Ground ( R-Y- G ) Fault Current :- Ir = 1.280kAmps, Iy = 1.220kAmps & Ig = 0.938kAmps Fault Distance :- 5.4 km towards Nalagarh from Prini. Line patrolling revealed an uprooted Devdar tree had fallen across the span between Tower No. 27 and 28 at Sajla Village, causing the snapping of the bottom conductor of 220 KV AD hydro (AD)-Phozal(HP) (ADHPL) Ckt-1. No abnormalities were detected in 220KV AD Hydro (AD) - Nallagarh (PG) (ADHPL) Ckt-1 during inspection. It was, therefore, concluded that the line must have tripped due to touching of some branches of the fallen tree while falling down. | There was a shortfall of 4.33 LU on 07.08.2025 & 1.01 LU on 08.08.2025 from the scheduled generation at ADHPL due to this outage. There was Generation Loss of 4.56 LU which includes the shortfall from the scheduled generation due to this outage. | Outage period and reason verified as per NRLDC records./210 MW Generation Loss | 3 | 0.065278
| ADHP0002 | 2 | 220 kV AD Hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2025-08-07 16:38 | 2025-08-08 18:59 | - | - | 1899-12-31 02:21 | - | LNCC | - | NR-2508-2044 | Line tripped, following paramters were observed: Fault Type: Double Phase to Ground (Y-B-G) fault. Fault Current: Iy = 2.587kAmps, Ib = 3.334kAmps & Ig = 0.981kAmps. Fault Distance: 5.4km towards Nalagarh from Prini. Line patrolling revealed an uprooted Devdar tree had fallen across the span between Tower No. 27 and 28 at Sajla Village, causing the snapping of the bottom conductor of 220 KV AD hydro (AD)-Phozal(HP) (ADHPL) Ckt-1. Photographs attached as Annex- IV with the mail. |  | Outage period and reason verified as per NRLDC records./210 MW Generation Loss | 3 | 1.0979
| ADHP0001 | 3 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-08-07 23:33 | 2025-08-08 00:20 | 0.032639 | - | - | - | LEFT | - | NR-2508-1805 | Line tripped, following paramters were observed: Fault Type: B-G (Phase to Ground). Fault Current: Ib-1.524 kA & In-1.465 kA. Fault Distance: 54.7 KM towards Nalagarh During line patrolling no abnormality was observed. Hence the fault might be transient in nature and may be due to inclement weather conditions in the nearby area. |  | Outage period and reason verified as per NRLDC records./210 MW Generation Loss
| ADHP0003 | 4 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-08-16 12:49 | 2025-08-16 13:43 | 0.0375 | - | - | - | LEFT | - | NR-2508-3534 | Line tripped, following paramters were observed: Fault type: Y phase to ground Fault location: 141 K M towards Phozal. Fault current: 0.972 kAmp | - | Outage period and reason verified as per NRLDC records.
| ADHP0001 | 5 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-08-20 11:08 | 2025-09-19 15:55 | - | - | 1900-01-29 04:47 | - | LNCC | - | NR-2509-4412 | Line tripped, following paramters were observed: Fault Type: B-G (Phase to Ground). Fault Current: Ib-2.062 kA & In-2.262 kA. Fault Distance: 40.0 km Line patrolling was conducted, which revealed that transmission line towers 157 and 158 of the AD Hydro line, located near Brehan village (approximately 40.0 km from AD Hydro), were collapsed after a big stone rolled down from the hill slope during a landslide. Photographs attached as Annex- V with the mail. This outage was in continuation from previous month since 11:08 Hours on 20.08.2025. After the temporary restoration works the line was successfully re-energized. | There was a shortfall of 27.07 LU on 20.08.2025 & 45.01 LU on 08.08.2025 from the scheduled generation at ADHPL due to this outage. Till now there is Generation Loss of 540.27 LU which includes the shortfall from the scheduled generation due to this outage. | Outage period and reason verified as per NRLDC records./210 MW Generation Loss | 12 | 30.1993
| ADHP0003 | 6 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-08-20 11:08 | 2025-10-08 13:33 | - | - | 1900-02-17 02:25 | - | LNCC | - | - | Line tripped, following paramters were observed at Phozal substion: 'Fault Type : R Phase to Ground Fault Location : 45 km towards Nalagarh Fault Current : 1698 Amp Line patrolling was conducted, which revealed that transmission line towers 157 and 158 of the AD Hydro line, located near Brehan village (approximately 40.0 km from AD Hydro), were collapsed after a big stone rolled down from the hill slope during a landslide. Photographs attached as Annex- V with the mail. This outage was in continuation since 11:08 Hours on 20.08.2025. The line has been successfully and permanently restored for its normal operation after restoration of Tower No.158 and removal of ERS system on 08.10.2025. However the line could not be energized till date due to the collapse of HPPTCL's Tower no. 1 on HPPTCL's portion of the line. The mail is attached for your reference as Annex VI |  | Outage period and reason verified as per NRLDC records./210 MW Generation Loss As per NRLDC records, line is under outage due to Tower collapse. No supporting documents receib=ved. No NRLC communication regarding charging has been done with NRLDC../Availability may be curtailed accordingly for full month of October.. | 50 | 49.1007
| ADHP0002 | 1 | 220 kV AD Hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2025-08-26 12:20 | 2025-09-25 13:37 | - | - | 1900-01-29 01:17 | - | LNCC | - | NR-2509-5989 | Due to cloud-burst and flash flood in Phojal Nallah, the Tower No.1 of HPPTCL D/C LILO 220 kV Phojal- Prini and Phojal – Nalagarh 6.7 km long transmission line has collapsed. This portion of line is maintained by HPPTCL therefore this outage is not attributable to ADHPL. | - | As per NRLDC records; tripping occurred at 11:08 Hrs from 20.08.2025./Further, tripping and outage duration must be curtailed of AD Hydro as per August available Data./Reason is 20 August 11:08 incident only./210 MW Generation loss(incident was not reported to OMS in August) | 50 | 30.0535
| ADHP0001 | 1 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-10-03 09:24 | 2025-10-03 17:10 | - | - | 0.32361 | - | LNCC | NR-2510-394 | NR-2510-506 | Removal of cross jumpers provided in the ERS arrangement at tower no.124 & 199 to restore the circuit to its normal configuartion. | - | Outage period and reason verified as per NRLDC records.
| ADHP0003 | 1 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2025-10-08 13:33 | 2026-01-01 | - | 1900-03-24 10:27 | - | - | OSFD | - | - | Due to cloud-burst and flash flood in Phojal Nallah, the Tower No.1 of HPPTCL D/C LILO 220 kV Phojal – Nalagarh 6.7 km long transmission line has collapsed. This portion of line is maintained by HPPTCL, therefore, this outage is not attributable to ADHPL. The line is still under outage. The mail is attached for your reference as Annex VI. | - | As per NRLDC records, line is under outage due to Tower collapse. No supporting documents receib=ved. No NRLC communication regarding charging has been done with NRLDC../Availability may be curtailed accordingly for full month of October.. | 50 | 84.4354
| ADHP0001 | 2 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2025-12-26 21:30 | 2025-12-26 23:03 | - | 0.064583 | - | - | OMSU | - | Closing Code- NR-2512-12802 | Line tripped due to tripping of C.B at Nalagarh end while the breaker at Prini end remained closed. No fault parameters were recorded at both ends. |  | As per NRLDC records; Reason of tripping is Phase to earth fault R-N , Zone-1 from AD Hydro. AD Hydro availability shall be curtailed accordingly. Time verified as per NRLDC records.
Formulas:
Hrs:Min = [RESTORATION]-[OUTAGE]
OTHERS = [RESTORATION]-[OUTAGE]

## I
Month | NORTHERN REGIONAL LOAD DESPATCH CENTRE
AD HYDRO POWER LIMITED
OUTAGE DUE TO PLANNED SHUTDOWN AND TRIPPING ATTRIBUTED TO SELF BY TRANSMISSION LICENSEE
| DURATION - Feb.-2026 |  |  | LINE/ ICT OUTAGE DETAILS
| ELEMENT CODE | EVENT NO. | ELEMENT NAME | OUTAGE | RESTORATION | DURATION OF OUTAGE ATTRIBUTABLE TO |  |  |  | Classification/ Category Code | NRLDC CODE |  | REASON OF OUTAGE | Shortfall from the scheduled Generation and Loss of Generation, if any. in kwh | NRLDC REMARKS | Availability %
|  |  |  | DATE TIME | DATE TIME | ADHPL | OTHERS | System constraint/ Natural calamity/ Militancy | Deemed Available
[6 empty] | @ (T) | # (U) | & ( C ) | * (D)
[6 empty] | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min | Code | OPENING | CLOSING
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 |  | 13
2026-02-01 | ADHP0003 | 1 | 220 kV Phozal(HP)-Nalagarh(PG) (ADHPL) Ckt-1 | 2026-02-01 | 2026-03-01 | - | 1900-01-27 | - | - | OSFD | - | - | Due to cloud-burst and flash flood in Phojal Nallah, the Tower No.1 of HPPTCL D/C LILO 220 kV Phojal – Nalagarh 6.7 km long transmission line has collapsed. This outage is continuation from 13:33 Hours on 08-10-2025. This portion of line is owned and maintained by HPPTCL, therefore, this outage is not attributable to ADHPL. The line is still under outage. The mail is attached for your reference as Annex VI. |  | Outage period and reason verified as per NRLDC records. | Awaited
| ADHP0001 | 1 | 220 kV AD Hydro(AD)-Nallagarh(PG) (ADHPL) Ckt-1 | 2026-02-09 10:49 | 2026-02-09 15:23 | 0.19028 | - | - | - | LHWT | Opening Code- NR-2602-3862 | Closing Code- NR-2602-3919 | Tightening work of loose jumpers. R Phase Jumper Broken sparking observed on the bottom jumper at Tower No. 198 in the Thraas area. |  | As per NRLDC records; Reason of tripping is Phase to earth fault R-N , Zone-1 from AD Hydro. AD Hydro availability shall be curtailed accordingly. Time verified as per NRLDC records.
| ADHP0002 | 2 | 220 kV AD Hydro(AD)-Phozal(HP) (ADHPL) Ckt-1 | 2026-02-28 10:20 | 2026-02-28 21:22 | - | 0.45972 | - | - | OSPD | Opening code: NR2602-13301 | Closing code: NR2602-13549 | OPGW Splicing & jointing work. The outage is planned and requested by SLDC-HP, therefore, this outage is not attributable to ADHPL.
Formulas:
OTHERS = [RESTORATION]-[OUTAGE]
DURATION OF OUTAGE ATTRIBUTABLE TO = [RESTORATION]-[OUTAGE]

## II
II. Elements where restoration time has exceeded the standards specified in Regulation 5 (b).
Element Name | Restoration time as specified in Regulation 5 (b) (in days) | Actual restoration time (in days) | Reason | OUTAGE | RESTORATION
Nil | Nil | Nil | Nil | Nil | Nil

## I_f (hidden)
I. AC Transmission Line/ ICT/ Static VAr Compensator/ Series Compensator/ HVDC (Back-to-Back Stations and Bi-Pole Links)/ Line Rectors/ Bus Reactors Outage Details for the month of ________
Element Name | Outage | Restoration | Duration of Outage Attributable to |  |  |  | Reason of Outage | % Availability
| Date Time | Date Time | Inter-State Transmission Licensee | Others | System constraint/ Natural calamity/ Militancy | Deemed Available
|  |  | Hrs:Min | Hrs:Min | Hrs:Min | Hrs:Min

## III
III. Details of compensation paid by the inter-State transmission licensee
Element Name | Violation of Regulation 5 (a) |  | Violation of Regulation 5 (b) |  | Compensation paid (in INR)
| % Availability prescribed | Actual % Availability | Restoration time prescribed (in days) | Actual restoration time (in days)
| 90 |  | Nil | Nil | Nil
Total

## IV
IV |  |  |  |  | Data to be furnished by the inter-State Transmission Licensees to POSOCO
1 |  |  |  |  | The Dependability Index defined as D=Nc/(Nc + Nf) where Nc is the number of correct operations during the given time interval and Nf is the number of failures to operate at internal power system faults.
2 |  |  |  |  | The Security Index defined as 􀜵 􀵌 􀯇􀳎 􁈺􀯇􀳎􀬾􀯇􀳠􁈻 where 􀜰􀯨 is the number of unwanted operations.
3 |  |  |  |  | The Reliability Index defined 􀜴 􀵌 􀯇􀳎 􁈺􀯇􀳎􀬾􀯇􀳔􁈻 where 􀜰􀯜 is the number of incorrect operations and is the sum of 􀜰􀯙 and 􀜰􀯨.
4 |  |  |  |  | From above 􀬵 􀯌 + 􀬵 􀮽 = 􀬵 􀯋 + 1
5 |  |  |  |  | The number of trippings of each transmission element. Five or more trippings of a transmission element in a month to be put on the website by the inter-State Transmission Licensees and reported to the Commission by POSOCO
Note:
1 |  |  |  |  | The data for these indices are presently prescribed for collection by the System Operator.
2 |  |  |  |  | These indices shall be computed by the POSOCO and furnished to the Commission on monthly basis.
Month | Nc | Nf | Nu | Ni | Depandablility Index (D) | Security Index (S) | Reliability Index ( R ) | 1/S+1/D=1/R+1
2026-02-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## V
V. Data to be compiled by the inter-State Transmission Licensees
The restoration times for different types of failures of a transmission line and failure of Inter-Connecting Transformer (ICT) and reactor in the following format:
-
-
Sl. | Types of failures | Restoration Time (Days)
No.
A. | Elements of the Transmission line for Single Circuit (S/C), Double Circuit (D/C) and Multi-Circuit (M/C) towers for each kV class separately
1 | Insulator failure | Terrain type
|  | Plain | River bed |  | Hilly
| (i) Insulator failure in single phase | - | - |  | -
| (ii) Insulator failure in two phases | - | - |  | -
| (iii) Insulator failure in three phases | - | - |  | -
2 | Tower after collapse by Emergency Restoration System (ERS) for S/C, D/C and M/C separately | - | - |  | -
3 | Tower after collapse without Emergency Restoration System (ERS) for S/C, D/C and M/C separately | - | - |  | -
4 | Tower damage (not collapse)
| One arm damage | - | - | - | -
| Two arms damage | - | - | - | -
5 | Snapping of phase conductor
| Conductor snapping in single phase | - | - | - | -
| Conductor snapping in two phases | - | - | - | -
| Conductor snapping in three phases | - | - | - | -
6 | Failure of earth wire | - | - | - | -
7 | Insulator failure with conductor snapping | - | - | - | -
8 | Any other combination of failures | - | - | - | -
B. | Elements of the sub-station for each kV class separately
1 | Failure of Inter Connecting Transformers (ICTs)
Restoration of the failed ICT
| Other major failures in ICTs | Single phase unit |  | Three phase unit
| (i) Replacement of faulty bushings | - | - | - | -
| (ii) Replacement of failed/ blasted bushings | - | - | - | -
| (iii) Replacement of faulty tap changers | - | - | - | -
2 | Failure of Reactors | - | - | - | -
| Restoration of the failed reactor | - | - | - | -